## Sheet1
DM-50 Register Map Ver 1.01
1 reg = | 2bytes (16bit)
short int = | 16 bit
int = | 32 bit
long int = | 64 bit
neg P = | export
neg Q = | capacitive
Instantaneous Parameter
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0000 | Ampere L1 | R | A | 0.001 | unsigned int |  | 4 | 0
0002 | Ampere L2 | R | A | 0.001 | unsigned int |  | 4 | 2
0004 | Ampere L3 | R | A | 0.001 | unsigned int |  | 4 | 4
0006 | Ampere Neutral | R | A | 0.001 | unsigned int |  | 4 | 6
0008 | Voltage L1 | R | V | 0.1 | unsigned int |  | 4 | 8
000A | Voltage L2 | R | V | 0.1 | unsigned int |  | 4 | 10
000C | Voltage L3 | R | V | 0.1 | unsigned int |  | 4 | 12
000E | Voltage L12 | R | V | 0.1 | unsigned int |  | 4 | 14
0010 | Voltage L23 | R | V | 0.1 | unsigned int |  | 4 | 16
0012 | Voltage L31 | R | V | 0.1 | unsigned int |  | 4 | 18
0014 | Empty | - |  |  |  |  | 2 | 20
0015 | Frequency | R | Hz | 0.01 | unsigned short int |  | 2 | 21
0016 | kW L1 | R | W | 0.1 | int | neg => export | 4 | 22
0018 | kW L2 | R | W | 0.1 | int |  | 4 | 24
001A | kW L3 | R | W | 0.1 | int |  | 4 | 26
001C | kVAr L1 | R | VAr | 0.1 | int | neg => capacitive | 4 | 28
001E | kVAr L2 | R | VAr | 0.1 | int |  | 4 | 30
0020 | kVAr L3 | R | VAr | 0.1 | int |  | 4 | 32
0022 | kVA L1 | R | VA | 0.1 | unsigned int |  | 4 | 34
0024 | kVA L2 | R | VA | 0.1 | unsigned int |  | 4 | 36
0026 | kVA L3 | R | VA | 0.1 | unsigned int |  | 4 | 38
0028 | PF L1 | R | - | 0.001 | short int | neg => capacitive | 2 | 40
0029 | PF L2 | R |  | 0.001 | short int |  | 2 | 41
002A | PF L3 | R |  | 0.001 | short int |  | 2 | 42
002B | PF Average | R |  | 0.001 | short int |  | 2 | 43
002C | Cos L1 | R |  | 0.001 | short int |  | 2 | 44
002D | Cos L2 | R |  | 0.001 | short int |  | 2 | 45
002E | Cos L3 | R |  | 0.001 | short int |  | 2 | 46
002F | Cos Average | R |  | 0.001 | short int |  | 2 | 47
Total Registers = 48
Setting Parameter
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Data Value | Reg Byte Count | Reg Addr (Dec)
0F00 | model | R | - | - | unsigned short int | fixed 0x1050 | 2 | 3840
0F01 | firmware Ver | R | - | 0.01 | unsigned short int | 101 | 2 | 3841
0F02 | ct ratio | R/W | - | 1 | unsigned short int | 1 ~ 2000 | 2 | 3842
0F03 | empty | - |  |  |  |  | 2 | 3843
0F04 | empty | [5 empty] | 2 | 3844
0F05 | mapping Ver | R | - | 0.01 | unsigned short int | 101 | 2 | 3845
0F06 | operation hour | R | min | 1 | unsigned int |  | 4 | 3846
0F08 | over Current | R/W | % | 1 | unsigned short int | OFF = 0 or 10 ~ 110 | 2 | 3848
0F09 | under Current | R/W | % | 1 | unsigned short int | OFF = 0 or 5 ~ 100 | 2 | 3849
0F0A | over Voltage | R/W | V | 1 | unsigned short int | OFF = 0 or 200 ~ 270 | 2 | 3850
0F0B | under Voltage | R/W | V | 1 | unsigned short int | OFF = 0 or 70 ~ 220 | 2 | 3851
0F0C | over Frequency | R/W | Hz | 1 | unsigned short int | OFF = 0 or 45 ~ 65 | 2 | 3852
0F0D | under Frequency | R/W | Hz | 1 | unsigned short int |  | 2 | 3853
0F0E | lo PF | R/W | - | 0.01 | short int | OFF = 0 or 85 ~ 100 cap (neg), 85 ~ 100 ind | 2 | 3854
0F0F | lo Cos | R/W |  | 0.01 | short int |  | 2 | 3855
0F10 | relay on time delay | R/W | s | 1 | unsigned short int | 1 ~ 200 | 2 | 3856
0F11 | relay off time delay | R/W | s | 1 | unsigned short int |  | 2 | 3857
0F12 | 1st general setting | R | - | 1 | unsigned short int |  | 2 | 3858
0F13 | 2nd general setting | R |  | 1 | unsigned short int |  | 2 | 3859
Total Registers = 20
2nd General Setting High Byte
| bit15 | bit14 | bit13 | bit12 | bit11 | bit10 | bit9 | bit8
| reserved for internal MCU setting (can be ignore) |  |  |  | Empty | Network Type | Scroll Phase | Empty
[5 empty] | - | 0 = 3P4W / 3P3W 1 = 1P2W | 0 = Off 1 = Auto | -
2nd General Setting Low Byte
| bit7 | bit6 | bit5 | bit4 | bit3 | bit2 | bit1 | bit0
Reserved
1st General Setting High Byte
| bit15 | bit14 | bit13 | bit12 | bit11 | bit10 | bit9 | bit8
Alarm Flag
| lo Cos | lo PF | under Frequency | over Frequency | under Voltage | over Voltage | under Current | over Current
1st General Setting Low Byte
| bit7 | bit6 | bit5 | bit4 | bit3 | bit2 | bit1 | bit0
| Empty |  |  |  |  | Default Parameter Display
| - |  |  |  |  | 000 = Ampere, 001 = Voltage, 010 = Frequency 011 = PF, 100 = Cos 101 = kW, 110 = kVAr, 111 = kVA