## Sheet1
PQM-1000s Register Map Ver 1.0.04
1reg = | 2bytes (16bit) |  |  |  |  | Modbus Error Code => | 1: non recognized function
short int = | 16 bit | [5 empty] | 2: data request out of range
integer = | 32 bit
long int = | 64 bit
neg P = | export
neg Q = | capacitive
Instantaneous Parameter
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0000 | Ampere L1 | R | A | 0.001 | unsigned int |  | 4 | 0
0002 | Ampere L2 | R | A | 0.001 | unsigned int |  | 4 | 2
0004 | Ampere L3 | R | A | 0.001 | unsigned int |  | 4 | 4
0006 | Ampere (Neutral current) | R | A | 0.001 | unsigned int |  | 4 | 6
0008 | Voltage L1 | R | V | 0.1 | unsigned int |  | 4 | 8
000A | Voltage L2 | R | V | 0.1 | unsigned int |  | 4 | 10
000C | Voltage L3 | R | V | 0.1 | unsigned int |  | 4 | 12
000E | Voltage L12 | R | V | 0.1 | unsigned int |  | 4 | 14
0010 | Voltage L23 | R | V | 0.1 | unsigned int |  | 4 | 16
0012 | Voltage L31 | R | V | 0.1 | unsigned int |  | 4 | 18
0014 | Voltage Assym | R | % | 0.1 | unsigned short int |  | 2 | 20
0015 | Frequency | R | Hz | 0.01 | unsigned short int |  | 2 | 21
0016 | kW L1 | R | W | 0.1 | int | neg => export | 4 | 22
0018 | kW L2 | R | W | 0.1 | int | neg => export | 4 | 24
001A | kW L3 | R | W | 0.1 | int | neg => export | 4 | 26
001C | kVar L1 | R | Var | 0.1 | int | neg => capacitive | 4 | 28
001E | kVar L2 | R | Var | 0.1 | int | neg => capacitive | 4 | 30
0020 | kVar L3 | R | Var | 0.1 | int | neg => capacitive | 4 | 32
0022 | kVA L1 | R | VA | 0.1 | unsigned int |  | 4 | 34
0024 | kVA L2 | R | VA | 0.1 | unsigned int |  | 4 | 36
0026 | kVA L3 | R | VA | 0.1 | unsigned int |  | 4 | 38
0028 | PF L1 | R | - | 0.001 | short int | neg => capacitive | 2 | 40
0029 | PF L2 | R | - | 0.001 | short int | neg => capacitive | 2 | 41
002A | PF L3 | R | - | 0.001 | short int | neg => capacitive | 2 | 42
002B | PF avg | R | - | 0.001 | short int | neg => capacitive | 2 | 43
002C | Cos L1 | R | - | 0.001 | short int | neg => capacitive | 2 | 44
002D | Cos L2 | R | - | 0.001 | short int | neg => capacitive | 2 | 45
002E | Cos L3 | R | - | 0.001 | short int | neg => capacitive | 2 | 46
002F | Cos avg | R | - | 0.001 | short int | neg => capacitive | 2 | 47
0030 | Energy Import (kWh) | R/W | kWh | 0.1 | unsigned int |  | 8 | 48
0034 | Energy Export (kWh) | R/W | kWh | 0.1 | unsigned int |  | 8 | 52
0038 | Energy Inductive (kVarh) | R/W | kVarh | 0.1 | unsigned int |  | 8 | 56
003C | Energy Capacitive (kVarh) | R/W | kVarh | 0.1 | unsigned int |  | 8 | 60
0040 | Energy Apparent (kVAh) | R/W | kVAh | 0.1 | unsigned int |  | 8 | 64
0044 | Max Dmd kW L1 (import) | R/W | W | 0.1 | unsigned int |  | 4 | 68
0046 | Max Dmd kW L2 (import) | R/W | W | 0.1 | unsigned int |  | 4 | 70
0048 | Max Dmd kW L3 (import) | R/W | W | 0.1 | unsigned int |  | 4 | 72
004A | Max Dmd kW Total (import) | R/W | W | 0.1 | unsigned int |  | 4 | 74
004C | Max Dmd kVA L1 | R/W | VA | 0.1 | unsigned int |  | 4 | 76
004E | Max Dmd kVA L2 | R/W | VA | 0.1 | unsigned int |  | 4 | 78
0050 | Max Dmd kVA L3 | R/W | VA | 0.1 | unsigned int |  | 4 | 80
0052 | Max Dmd kVA Total | R/W | VA | 0.1 | unsigned int |  | 4 | 82
0054 | Max Dmd I L1 | R/W | A | 0.001 | unsigned int |  | 4 | 84
0056 | Max Dmd I L2 | R/W | A | 0.001 | unsigned int |  | 4 | 86
0058 | Max Dmd I L3 | R/W | A | 0.001 | unsigned int |  | 4 | 88
005A | Max Dmd Iavg (3phase) | R/W | A | 0.001 | unsigned int |  | 4 | 90
005C | Prev Dmd kW L1 (import) | R/W | W | 0.1 | unsigned int |  | 4 | 92
005E | Prev Dmd kW L2 (import) | R/W | W | 0.1 | unsigned int |  | 4 | 94
0060 | Prev Dmd kW L3 (import) | R/W | W | 0.1 | unsigned int |  | 4 | 96
0062 | Prev Dmd kW Total (import) | R/W | W | 0.1 | unsigned int |  | 4 | 98
0064 | Prev Dmd kVA L1 | R/W | VA | 0.1 | unsigned int |  | 4 | 100
0066 | Prev Dmd kVA L2 | R/W | VA | 0.1 | unsigned int |  | 4 | 102
0068 | Prev Dmd kVA L3 | R/W | VA | 0.1 | unsigned int |  | 4 | 104
006A | Prev Dmd kVA Total | R/W | VA | 0.1 | unsigned int |  | 4 | 106
006C | Prev Dmd I L1 | R/W | A | 0.001 | unsigned int |  | 4 | 108
006E | Prev Dmd I L2 | R/W | A | 0.001 | unsigned int |  | 4 | 110
0070 | Prev Dmd I L3 | R/W | A | 0.001 | unsigned int |  | 4 | 112
0072 | Prev Dmd Iavg (3phase) | R/W | A | 0.001 | unsigned int |  | 4 | 114
0074 | Demand Elapsed Time | R/W | sec | 1 | unsigned short int |  | 2 | 116
0075 | THD V1 | R | % | 0.1 | unsigned short int |  | 2 | 117
0076 | THD V2 | R | % | 0.1 | unsigned short int |  | 2 | 118
0077 | THD V3 | R | % | 0.1 | unsigned short int |  | 2 | 119
0078 | THD I1 | R | % | 0.1 | unsigned short int |  | 2 | 120
0079 | THD I2 | R | % | 0.1 | unsigned short int |  | 2 | 121
007A | THD I3 | R | % | 0.1 | unsigned short int |  | 2 | 122
007B | kf I1 | R | - | 0.01 | unsigned short int |  | 2 | 123
007C | kf I2 | R | - | 0.01 | unsigned short int |  | 2 | 124
007D | kf I2 | R | - | 0.01 | unsigned short int |  | 2 | 125
[6 empty] | total bytes | 252
Instantaneous Parameter
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0080 | V L1 angle | R | deg | 0.1 | short int | 0 ~ - 359.9 | 2 | 128
0081 | V L2 angle | R | deg | 0.1 | short int | 0 ~ - 359.9 | 2 | 129
0082 | V L3 angle | R | deg | 0.1 | short int | 0 ~ - 359.9 | 2 | 130
0083 | I L1 angle | R | deg | 0.1 | short int | 0 ~ - 359.9 | 2 | 131
0084 | I L2 angle | R | deg | 0.1 | short int | 0 ~ - 359.9 | 2 | 132
0085 | I L3 angle | R | deg | 0.1 | short int | 0 ~ - 359.9 | 2 | 133
0086 | In angle (neutral) | R | deg | 0.1 | short int | 0 ~ - 359.9 | 2 | 134
0087 | Phase Rotation | R | - | - | short int | bit<1> = 1 => clockwise, bit<0> = 1 => valid sequence | 2 | 135
0088 | hour run | R | sec | 1 | unsigned int |  | 4 | 136
[6 empty] | total bytes | 20
Min / Max Parameter
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0200 | V L1 min | R/W | V | 0.1 | unsigned int |  | 4 | 512
0202 | V L2 min | R/W | V | 0.1 | unsigned int |  | 4 | 514
0204 | V L3 min | R/W | V | 0.1 | unsigned int |  | 4 | 516
0206 | V L1 max | R/W | V | 0.1 | unsigned int |  | 4 | 518
0208 | V L2 max | R/W | V | 0.1 | unsigned int |  | 4 | 520
020A | V L3 max | R/W | V | 0.1 | unsigned int |  | 4 | 522
020C | V assym min | R/W | % | 0.1 | unsigned short int |  | 2 | 524
020D | V assym max | R/W | % | 0.1 | unsigned short int |  | 2 | 525
020E | I L1 min | R/W | A | 0.001 | unsigned int |  | 4 | 526
0210 | I L2 min | R/W | A | 0.001 | unsigned int |  | 4 | 528
0212 | I L3 min | R/W | A | 0.001 | unsigned int |  | 4 | 530
0214 | I n min | R/W | A | 0.001 | unsigned int |  | 4 | 532
0216 | I L1 max | R/W | A | 0.001 | unsigned int |  | 4 | 534
0218 | I L2 max | R/W | A | 0.001 | unsigned int |  | 4 | 536
021A | I L3 max | R/W | A | 0.001 | unsigned int |  | 4 | 538
021C | I n max | R/W | A | 0.001 | unsigned int |  | 4 | 540
021E | kW L1 min (import) | R/W | W | 0.1 | unsigned int |  | 4 | 542
0220 | kW L2 min (import) | R/W | W | 0.1 | unsigned int |  | 4 | 544
0222 | kW L3 min (import) | R/W | W | 0.1 | unsigned int |  | 4 | 546
0224 | kW total min (import) | R/W | W | 0.1 | unsigned int |  | 4 | 548
0226 | kW L1 max (import) | R/W | W | 0.1 | unsigned int |  | 4 | 550
0228 | kW L2 max (import) | R/W | W | 0.1 | unsigned int |  | 4 | 552
022A | kW L3 max (import) | R/W | W | 0.1 | unsigned int |  | 4 | 554
022C | kW total max (import) | R/W | W | 0.1 | unsigned int |  | 4 | 556
022E | THD V L1 min | R/W | % | 0.1 | unsigned int |  | 2 | 558
022F | THD V L2 min | R/W | % | 0.1 | unsigned int |  | 2 | 559
0230 | THD V L3 min | R/W | % | 0.1 | unsigned int |  | 2 | 560
0231 | THD V L1 max | R/W | % | 0.1 | unsigned int |  | 2 | 561
0232 | THD V L2 max | R/W | % | 0.1 | unsigned int |  | 2 | 562
0233 | THD V L3 max | R/W | % | 0.1 | unsigned int |  | 2 | 563
0234 | THD I L1 min | R/W | % | 0.1 | unsigned int |  | 2 | 564
0235 | THD I L2 min | R/W | % | 0.1 | unsigned int |  | 2 | 565
0236 | THD I L3 min | R/W | % | 0.1 | unsigned int |  | 2 | 566
0237 | THD I L1 max | R/W | % | 0.1 | unsigned int |  | 2 | 567
0238 | THD I L2 max | R/W | % | 0.1 | unsigned int |  | 2 | 568
0239 | THD I L3 max | R/W | % | 0.1 | unsigned int |  | 2 | 569
023A | Vmax Elapsed | R | s | 1 | unsigned int |  | 4 | 570
023C | Imax Elapsed | R | s | 1 | unsigned int |  | 4 | 572
023E | THD Vmax Elapsed | R | s | 1 | unsigned int |  | 4 | 574
0240 | THD Imax Elapsed | R | s | 1 | unsigned int |  | 4 | 576
[6 empty] | total bytes | 132
Voltage Harmonic Spectrum Parameter (Secondary Value)
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0300 | V L1-Spectrum H-order 1 | R | V | 0.1 * vtr | unsigned int | Actual Value = | 2 | 768
0301 | V L1-Spectrum H-order 3 | R | V | 0.1 * vtr | unsigned int | Reg Val * vtr * 0.1 | 2 | 769
0302 | V L1-Spectrum H-order 5 | R | V | 0.1 * vtr | unsigned int |  | 2 | 770
0303 | V L1-Spectrum H-order 7 | R | V | 0.1 * vtr | unsigned int |  | 2 | 771
0304 | V L1-Spectrum H-order 9 | R | V | 0.1 * vtr | unsigned int |  | 2 | 772
0305 | V L1-Spectrum H-order 11 | R | V | 0.1 * vtr | unsigned int |  | 2 | 773
0306 | V L1-Spectrum H-order 13 | R | V | 0.1 * vtr | unsigned int |  | 2 | 774
0307 | V L1-Spectrum H-order 15 | R | V | 0.1 * vtr | unsigned int |  | 2 | 775
0308 | V L1-Spectrum H-order 17 | R | V | 0.1 * vtr | unsigned int |  | 2 | 776
0309 | V L1-Spectrum H-order 19 | R | V | 0.1 * vtr | unsigned int |  | 2 | 777
030A | V L1-Spectrum H-order 21 | R | V | 0.1 * vtr | unsigned int |  | 2 | 778
030B | V L1-Spectrum H-order 23 | R | V | 0.1 * vtr | unsigned int |  | 2 | 779
030C | V L1-Spectrum H-order 25 | R | V | 0.1 * vtr | unsigned int |  | 2 | 780
030D | V L1-Spectrum H-order 27 | R | V | 0.1 * vtr | unsigned int |  | 2 | 781
030E | V L1-Spectrum H-order 29 | R | V | 0.1 * vtr | unsigned int |  | 2 | 782
030F | V L1-Spectrum H-order 31 | R | V | 0.1 * vtr | unsigned int |  | 2 | 783
0310 | V L2-Spectrum H-order 1 | R | V | 0.1 * vtr | unsigned int |  | 2 | 784
0311 | V L2-Spectrum H-order 3 | R | V | 0.1 * vtr | unsigned int |  | 2 | 785
0312 | V L2-Spectrum H-order 5 | R | V | 0.1 * vtr | unsigned int |  | 2 | 786
0313 | V L2-Spectrum H-order 7 | R | V | 0.1 * vtr | unsigned int |  | 2 | 787
0314 | V L2-Spectrum H-order 9 | R | V | 0.1 * vtr | unsigned int |  | 2 | 788
0315 | V L2-Spectrum H-order 11 | R | V | 0.1 * vtr | unsigned int |  | 2 | 789
0316 | V L2-Spectrum H-order 13 | R | V | 0.1 * vtr | unsigned int |  | 2 | 790
0317 | V L2-Spectrum H-order 15 | R | V | 0.1 * vtr | unsigned int |  | 2 | 791
0318 | V L2-Spectrum H-order 17 | R | V | 0.1 * vtr | unsigned int |  | 2 | 792
0319 | V L2-Spectrum H-order 19 | R | V | 0.1 * vtr | unsigned int |  | 2 | 793
031A | V L2-Spectrum H-order 21 | R | V | 0.1 * vtr | unsigned int |  | 2 | 794
031B | V L2-Spectrum H-order 23 | R | V | 0.1 * vtr | unsigned int |  | 2 | 795
031C | V L2-Spectrum H-order 25 | R | V | 0.1 * vtr | unsigned int |  | 2 | 796
031D | V L2-Spectrum H-order 27 | R | V | 0.1 * vtr | unsigned int |  | 2 | 797
031E | V L2-Spectrum H-order 29 | R | V | 0.1 * vtr | unsigned int |  | 2 | 798
031F | V L2-Spectrum H-order 31 | R | V | 0.1 * vtr | unsigned int |  | 2 | 799
0320 | V L3-Spectrum H-order 1 | R | V | 0.1 * vtr | unsigned int |  | 2 | 800
0321 | V L3-Spectrum H-order 3 | R | V | 0.1 * vtr | unsigned int |  | 2 | 801
0322 | V L3-Spectrum H-order 5 | R | V | 0.1 * vtr | unsigned int |  | 2 | 802
0323 | V L3-Spectrum H-order 7 | R | V | 0.1 * vtr | unsigned int |  | 2 | 803
0324 | V L3-Spectrum H-order 9 | R | V | 0.1 * vtr | unsigned int |  | 2 | 804
0325 | V L3-Spectrum H-order 11 | R | V | 0.1 * vtr | unsigned int |  | 2 | 805
0326 | V L3-Spectrum H-order 13 | R | V | 0.1 * vtr | unsigned int |  | 2 | 806
0327 | V L3-Spectrum H-order 15 | R | V | 0.1 * vtr | unsigned int |  | 2 | 807
0328 | V L3-Spectrum H-order 17 | R | V | 0.1 * vtr | unsigned int |  | 2 | 808
0329 | V L3-Spectrum H-order 19 | R | V | 0.1 * vtr | unsigned int |  | 2 | 809
032A | V L3-Spectrum H-order 21 | R | V | 0.1 * vtr | unsigned int |  | 2 | 810
032B | V L3-Spectrum H-order 23 | R | V | 0.1 * vtr | unsigned int |  | 2 | 811
032C | V L3-Spectrum H-order 25 | R | V | 0.1 * vtr | unsigned int |  | 2 | 812
032D | V L3-Spectrum H-order 27 | R | V | 0.1 * vtr | unsigned int |  | 2 | 813
032E | V L3-Spectrum H-order 29 | R | V | 0.1 * vtr | unsigned int |  | 2 | 814
032F | V L3-Spectrum H-order 31 | R | V | 0.1 * vtr | unsigned int |  | 2 | 815
0330 | THD V1 | R | % | 0.1 | unsigned short int |  | 2 | 816
0331 | THD V2 | R | % | 0.1 | unsigned short int |  | 2 | 817
0332 | THD V3 | R | % | 0.1 | unsigned short int |  | 2 | 818
[6 empty] | total bytes | 102
Ampere Harmonic Spectrum Parameter (Secondary Value)
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0400 | I L1-Spectrum H-order 1 | R | A | 0.001*ctr | unsigned int | Actual value = | 2 | 1024
0401 | I L1-Spectrum H-order 3 | R | A | 0.001*ctr | unsigned int | Reg Val * ctr * 0.001 | 2 | 1025
0402 | I L1-Spectrum H-order 5 | R | A | 0.001*ctr | unsigned int |  | 2 | 1026
0403 | I L1-Spectrum H-order 7 | R | A | 0.001*ctr | unsigned int |  | 2 | 1027
0404 | I L1-Spectrum H-order 9 | R | A | 0.001*ctr | unsigned int |  | 2 | 1028
0405 | I L1-Spectrum H-order 11 | R | A | 0.001*ctr | unsigned int |  | 2 | 1029
0406 | I L1-Spectrum H-order 13 | R | A | 0.001*ctr | unsigned int |  | 2 | 1030
0407 | I L1-Spectrum H-order 15 | R | A | 0.001*ctr | unsigned int |  | 2 | 1031
0408 | I L1-Spectrum H-order 17 | R | A | 0.001*ctr | unsigned int |  | 2 | 1032
0409 | I L1-Spectrum H-order 19 | R | A | 0.001*ctr | unsigned int |  | 2 | 1033
040A | I L1-Spectrum H-order 21 | R | A | 0.001*ctr | unsigned int |  | 2 | 1034
040B | I L1-Spectrum H-order 23 | R | V | 0.001*ctr | unsigned int |  | 2 | 1035
040C | I L1-Spectrum H-order 25 | R | V | 0.001*ctr | unsigned int |  | 2 | 1036
040D | I L1-Spectrum H-order 27 | R | V | 0.001*ctr | unsigned int |  | 2 | 1037
040E | I L1-Spectrum H-order 29 | R | V | 0.001*ctr | unsigned int |  | 2 | 1038
040F | I L1-Spectrum H-order 31 | R | V | 0.001*ctr | unsigned int |  | 2 | 1039
0410 | I L2-Spectrum H-order 1 | R | A | 0.001*ctr | unsigned int |  | 2 | 1040
0411 | I L2-Spectrum H-order 3 | R | A | 0.001*ctr | unsigned int |  | 2 | 1041
0412 | I L2-Spectrum H-order 5 | R | A | 0.001*ctr | unsigned int |  | 2 | 1042
0413 | I L2-Spectrum H-order 7 | R | A | 0.001*ctr | unsigned int |  | 2 | 1043
0414 | I L2-Spectrum H-order 9 | R | A | 0.001*ctr | unsigned int |  | 2 | 1044
0415 | I L2-Spectrum H-order 11 | R | A | 0.001*ctr | unsigned int |  | 2 | 1045
0416 | I L2-Spectrum H-order 13 | R | A | 0.001*ctr | unsigned int |  | 2 | 1046
0417 | I L2-Spectrum H-order 15 | R | A | 0.001*ctr | unsigned int |  | 2 | 1047
0418 | I L2-Spectrum H-order 17 | R | A | 0.001*ctr | unsigned int |  | 2 | 1048
0419 | I L2-Spectrum H-order 19 | R | A | 0.001*ctr | unsigned int |  | 2 | 1049
041A | I L2-Spectrum H-order 21 | R | A | 0.001*ctr | unsigned int |  | 2 | 1050
041B | I L2-Spectrum H-order 23 | R | V | 0.001*ctr | unsigned int |  | 2 | 1051
041C | I L2-Spectrum H-order 25 | R | V | 0.001*ctr | unsigned int |  | 2 | 1052
041D | I L2-Spectrum H-order 27 | R | V | 0.001*ctr | unsigned int |  | 2 | 1053
041E | I L2-Spectrum H-order 29 | R | V | 0.001*ctr | unsigned int |  | 2 | 1054
041F | I L2-Spectrum H-order 31 | R | V | 0.001*ctr | unsigned int |  | 2 | 1055
0420 | I L3-Spectrum H-order 1 | R | A | 0.001*ctr | unsigned int |  | 2 | 1056
0421 | I L3-Spectrum H-order 3 | R | A | 0.001*ctr | unsigned int |  | 2 | 1057
0422 | I L3-Spectrum H-order 5 | R | A | 0.001*ctr | unsigned int |  | 2 | 1058
0423 | I L3-Spectrum H-order 7 | R | A | 0.001*ctr | unsigned int |  | 2 | 1059
0424 | I L3-Spectrum H-order 9 | R | A | 0.001*ctr | unsigned int |  | 2 | 1060
0425 | I L3-Spectrum H-order 11 | R | A | 0.001*ctr | unsigned int |  | 2 | 1061
0426 | I L3-Spectrum H-order 13 | R | A | 0.001*ctr | unsigned int |  | 2 | 1062
0427 | I L3-Spectrum H-order 15 | R | A | 0.001*ctr | unsigned int |  | 2 | 1063
0428 | I L3-Spectrum H-order 17 | R | A | 0.001*ctr | unsigned int |  | 2 | 1064
0429 | I L3-Spectrum H-order 19 | R | V | 0.001*ctr | unsigned int |  | 2 | 1065
042A | I L3-Spectrum H-order 21 | R | V | 0.001*ctr | unsigned int |  | 2 | 1066
042B | I L3-Spectrum H-order 23 | R | V | 0.001*ctr | unsigned int |  | 2 | 1067
042C | I L3-Spectrum H-order 25 | R | V | 0.001*ctr | unsigned int |  | 2 | 1068
042D | I L3-Spectrum H-order 27 | R | V | 0.001*ctr | unsigned int |  | 2 | 1069
042E | I L3-Spectrum H-order 29 | R | A | 0.001*ctr | unsigned int |  | 2 | 1070
042F | I L3-Spectrum H-order 31 | R | A | 0.001*ctr | unsigned int |  | 2 | 1071
0430 | THD I1 | R | % | 0.1 | unsigned short int |  | 2 | 1072
0431 | THD I2 | R | % | 0.1 | unsigned short int |  | 2 | 1073
0432 | THD I3 | R | % | 0.1 | unsigned short int |  | 2 | 1074
0433 | kf I1 | R | - | 0.01 | unsigned short int |  | 2 | 1075
0434 | kf I2 | R | - | 0.01 | unsigned short int |  | 2 | 1076
0435 | kf I2 | R | - | 0.01 | unsigned short int |  | 2 | 1077
[6 empty] | total bytes | 108
L1 Voltage Waveform (2 cycle waveform - scaled down 8bits / data point: Total 128pts)
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0500 | Waveform Definition<2:0> | R | - | 1 | unsigned short int | bit<1:0>= 00 => L1, bit<2>=0 => Voltage | 2 | 1280
0501 | V L1 phasor angle | R | deg | 0.1 | short int | 0 ~ - 359.9 | 2 | 1281
0502 | THD-V1 | R | % | 0.1 | unsigned short int |  | 2 | 1282
0503 | Voltage L1 | R | V | 0.1 | unsigned int |  | 4 | 1283
0505 | V data pt<1:0> | R | - | 1 | signed bytes * 2 |  | 2 | 1285
. . . | . . . (up to) |  | - |  |  |  | 124 | 1286
0544 | V data pt<127:126> | R/W |  | 1 | signed bytes * 2 |  | 2 | 1348
[6 empty] | total bytes | 138
L1 Ampere Waveform (2 cycle waveform - scaled down 8bits / data point: Total 128pts)
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0580 | Waveform Definition<2:0> | R | - | 1 | unsigned short int | bit<1:0>= 00 => L1, bit<2>=1 => Ampere | 2 | 1408
0581 | I L1 phasor angle | R | deg | 0.1 | short int | 0 ~ - 359.9 | 2 | 1409
0582 | THD-I1 | R | % | 0.1 | unsigned short int |  | 2 | 1410
0583 | Ampere L1 | R | A | 0.001 | unsigned int |  | 4 | 1411
0585 | I data pt<1:0> | R | - | 1 | signed bytes * 2 |  | 2 | 1413
. . . | . . . (up to) |  | - |  |  |  | 124 | 1414
05C4 | I data pt<127:126> | R/W |  | 1 | signed bytes * 2 |  | 2 | 1476
[6 empty] | total bytes | 138
L2 Voltage Waveform (2 cycle waveform - scaled down 8bits / data point: Total 128pts)
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0600 | Waveform Definition<2:0> | R | - | 1 | unsigned short int | bit<1:0>= 01 => L2, bit<2>=0 => Voltage | 2 | 1536
0601 | V L2 phasor angle | R | deg | 0.1 | short int | 0 ~ - 359.9 | 2 | 1537
0602 | THD-V2 | R | % | 0.1 | unsigned short int |  | 2 | 1538
0603 | Voltage L2 | R | V | 0.1 | unsigned int |  | 4 | 1539
0605 | V data pt<1:0> | R | - | 1 | signed bytes * 2 |  | 2 | 1541
. . . | . . . (up to) |  | - |  |  |  | 124 | 1542
0644 | V data pt<127:126> | R/W |  | 1 | signed bytes * 2 |  | 2 | 1604
[6 empty] | total bytes | 138
L2 Ampere Waveform (2 cycle waveform - scaled down 8bits / data point: Total 128pts)
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0680 | Waveform Definition<2:0> | R | - | 1 | unsigned short int | bit<1:0>= 01 => L2, bit<2>=1 => Ampere | 2 | 1664
0681 | I L2 phasor angle | R | deg | 0.1 | short int | 0 ~ - 359.9 | 2 | 1665
0682 | THD-I2 | R | % | 0.1 | unsigned short int |  | 2 | 1666
0683 | Ampere L2 | R | A | 0.001 | unsigned int |  | 4 | 1667
0685 | I data pt<1:0> | R | - | 1 | signed bytes * 2 |  | 2 | 1669
. . . | . . . (up to) |  | - |  |  |  | 124 | 1670
06C4 | I data pt<127:126> | R/W |  | 1 | signed bytes * 2 |  | 2 | 1732
[6 empty] | total bytes | 138
L3 Voltage Waveform (2 cycle waveform - scaled down 8bits / data point: Total 128pts)
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0700 | Waveform Definition<2:0> | R | - | 1 | unsigned short int | bit<1:0>= 10 => L3, bit<2>=0 => Voltage | 2 | 1792
0701 | V L3 phasor angle | R | deg | 0.1 | short int | 0 ~ - 359.9 | 2 | 1793
0702 | THD-V3 | R | % | 0.1 | unsigned short int |  | 2 | 1794
0703 | Voltage L3 | R | V | 0.1 | unsigned int |  | 4 | 1795
0705 | V data pt<1:0> | R | - | 1 | signed bytes * 2 |  | 2 | 1797
. . . | . . . (up to) |  | - |  |  |  | 124 | 1798
0744 | V data pt<127:126> | R/W |  | 1 | signed bytes * 2 |  | 2 | 1860
[6 empty] | total bytes | 138
L3 Ampere Waveform (2 cycle waveform - scaled down 8bits / data point: Total 128pts)
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0780 | Waveform Definition<2:0> | R | - | 1 | unsigned short int | bit<1:0>= 10 => L3, bit<2>=1 => Ampere | 2 | 1920
0781 | I L3 phasor angle | R | deg | 0.1 | short int | 0 ~ - 359.9 | 2 | 1921
0782 | THD-I3 | R | % | 0.1 | unsigned short int |  | 2 | 1922
0783 | Ampere L3 | R | A | 0.001 | unsigned int |  | 4 | 1923
0785 | I data pt<1:0> | R | - | 1 | signed bytes * 2 |  | 2 | 1925
. . . | . . . (up to) |  | - |  |  |  | 124 | 1926
07C4 | I data pt<127:126> | R/W |  | 1 | signed bytes * 2 |  | 2 | 1988
[6 empty] | total bytes | 138
Alternative Addr Setting Parameter
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0F00 | Device Code | R | - | 1 | unsigned short int | fixed 0x0001 | 2 | 3840
0F01 | Version | R | - | - | unsigned short int | 1006 | 2 | 3841
0F02 | CT Ratio (ctr) | R/W | - | 1 | unsigned short int | 0 ~ 2000 | 2 | 3842
0F03 | VT Ratio (vtr) | R/W | - | 0.1 | unsigned short int | 10 ~ 25000 | 2 | 3843
0F04 | Demand Interval | R/W | min | 1 | unsigned short int | 10 ~ 60 | 2 | 3844
[6 empty] | total bytes | 10
Setting Parameter
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
FF00 | Device Code | R | - | 1 | unsigned short int | fixed 0x0001 | 2 | 65280
FF01 | Version | R | - | - | unsigned short int | 1006 | 2 | 65281
FF02 | CT Ratio (ctr) | R/W | - | 1 | unsigned short int | 0 ~ 2000 | 2 | 65282
FF03 | VT Ratio (vtr) | R/W | - | 0.1 | unsigned short int | 10 ~ 25000 | 2 | 65283
FF04 | Demand Interval | R/W | min | 1 | unsigned short int | 10 ~ 60 | 2 | 65284
[6 empty] | total bytes | 10