## CapSizing
Capacitor Sizing & Selection
Enter Parameters Here
|  |  | MD : | 120 | kW
|  |  | Initial PF : | 0.7
|  |  | Target PF : | 0.95
|  |  | Load Factor (% MD) : | 100 | %
|  |  | Recommended CT Range : | 200 - | 250
|  |  | CT size Selection : | Auto | / 5A |  |  | NV-xx - The Smarter Choice for Automatic Power Factor Correction
|  |  | Cap rated Voltage : | 440 | Vac |  |  | Extremely user friendly with a host of features (THD & THD spectrum measurement, exhaust FAN control, smart Switching Sequence, auto CK, Alarm, operation from 1% load, capicitor usage stats, etc)
|  |  | Network Voltage (L-L) : | 415 | Vac
|  |  | 1st Step Cap Size : | Auto |  |  |  | PQM-1000s - The Smarter Choice for Power Quality Monitoring
|  |  | Harmonic Filter : | None |  |  |  | Extremely user friendly with many hi-End features (Waveform view, 360 Phasor view, THD Specturm Bar graph view, all relevant electrical Parameters, external plug-in-type RS-485 module, etc)
[22 empty] | Lfactor | 0
[8 empty] | DP-xx series Protection Relay - Best in Class | [13 empty] | deltaSize | 25
[8 empty] | Extremely user friendly controls for easy parameter setting and viewing (superior tripping response to short circuit with SPARC, trip events history with last tripped elapsed time, fault events history, external plug-in-type RS-485 module, etc) | [13 empty] | surgeF | 1.15
|  |  | CT Size : | 250 | / 5A | [13 empty] | Valid
|  |  | Required kVar : | 93 | kVar / | 440V | [12 empty] | Invalid |  |  |  |  | surge A = | 2 | x
|  | Switching Program | Capacitor Steps (kVar) | [13 empty] | Total kVar | Number of Steps | Total Cap Ampere | Recommeded MCCB Size | Size of Last Step | Amp of Last Step | MCCB Size | MCCB ReSized
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14
|  | 1:1:1:1:1 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 35 | --- | --- | --- | 2.5 | 3.09 | 0 | --- | #VALUE!
|  | 1:2:2:2:2 | 2.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 67.5 | --- | --- | --- | 5 | 6.19 | 0 | --- | #VALUE!
|  | 1:2:4:4:4 | 2.5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 97.5 | 11 | 120.6665 | 200 | 10 | 12.38 | 200 | 200 | 133.0465
|  | 1:1:2:2:2 | 2.5 | 2.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 65 | --- | --- | --- | 5 | 6.19 | 0 | --- | #VALUE!
|  | 1:1:2:2:4 | 2.5 | 2.5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 95 | 12 | 117.5725 | 200 | 10 | 12.38 | 200 | 200 | 129.9525
|  | 1:1:1:2:2 | 2.5 | 2.5 | 2.5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 62.5 | --- | --- | --- | 5 | 6.19 | 0 | --- | #VALUE!
|  | 1:2:4:8:8 | 2.5 | 5 | 10 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.5 | 7 | 120.6665 | 200 | 20 | 24.75 | 200 | 200 | 145.4165
| Note: | The above selection / option is only provided as a guideline for capacitor step & size selection. Actual load condition may vary and require different combination / selection of capacitor steps & sizes. | [17 empty] | Doc Version: 1.02
Caps
Auto
2.5 | 100 | P-1 | [14 empty] | 14 | bar: Capacitor Steps (kVar) 1 to Capacitor Steps (kVar) 14
5 | 80 | P-2 | [14 empty] | 14 | bar: Capacitor Steps (kVar) 1 to Capacitor Steps (kVar) 14
10 | 60 | P-3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 11
15 | 50 | P-4 | [14 empty] | 14 | bar: Capacitor Steps (kVar) 1 to Capacitor Steps (kVar) 14
20 | 40 | P-5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 12
25 | 30 | P-6 | [14 empty] | 14 | bar: Capacitor Steps (kVar) 1 to Capacitor Steps (kVar) 14
30 | 25 | P-7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7
40 | 20
50 | 15
60 | 10
80 | 5 |  | Capacitor Steps (kVar) 1: Sq(Vs/Vr) :; Capacitor Steps (kVar) 2: 0.88959; Capacitor Steps (kVar) 7: recommended
100 | 2.5 |  | Capacitor Steps (kVar) 1: Nominal MD :; Capacitor Steps (kVar) 2: 120; Capacitor Steps (kVar) 3: kW; Capacitor Steps (kVar) 5: CT Lo; Capacitor Steps (kVar) 6: 178; Capacitor Steps (kVar) 7: 200
|  |  | 1st Cap : | 2.5 | kVar |  | CT Hi | 223 | 250
None |  |  | Capacitor Steps (kVar) 1: 1st Cap Amp :; Capacitor Steps (kVar) 2: 3.094; Capacitor Steps (kVar) 3: A
6 |  |  | Capacitor Steps (kVar) 2: rated V actual; Capacitor Steps (kVar) 3: rated V Cap; Capacitor Steps (kVar) 4: Amp
7 |  |  | Capacitor Steps (kVar) 1: 1% cap :; Capacitor Steps (kVar) 2: 1.797; Capacitor Steps (kVar) 3: 2.02; Capacitor Steps (kVar) 4: 2.5; Capacitor Steps (kVar) 5: Limit (10%); Capacitor Steps (kVar) 7: 13%
13 |  |  | Capacitor Steps (kVar) 1: TotCapReq :; Capacitor Steps (kVar) 2: 83; Capacitor Steps (kVar) 3: 93; Capacitor Steps (kVar) 5: Q_L; Capacitor Steps (kVar) 6: 83; Capacitor Steps (kVar) 7: 78
[7 empty] | Q_H | 102 | 108
ct |  |  | Capacitor Steps (kVar) 1: look up 1st cap :; Capacitor Steps (kVar) 2: 2.5; Capacitor Steps (kVar) 3: kVar; Capacitor Steps (kVar) 4: 3.094
Auto |  |  | Capacitor Steps (kVar) 1: CT Value :; Capacitor Steps (kVar) 2: 250
60 | 10000
80 | 8000
100 | 6000
150 | 5000
200 | 4000
250 | 3000
300 | 2500
400 | 2000
500 | 1600
600 | 1500
800 | 1200
1000 | 1000
1200 | 800
1500 | 600
1600 | 500
2000 | 400
2500 | 300
3000 | 250
4000 | 200
5000 | 150
6000 | 100
8000 | 80
10000 | 60
Power Factor Controller
Power Quality Analyzer
Protection Relay