## Sheet1
Nv-5 Register Map Ver 1.00
1 reg = | 2bytes (16bit)
short int = | 16 bit
int = | 32 bit
long int = | 64 bit
neg P = | export
neg Q = | capacitive
Instantaneous Parameter
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0000 | Reserved | - |  |  | unsigned short int |  | 2 | 0
0001 | Voltage | R | V | 0.1 | unsigned short int |  | 2 | 1
0002 | Ampere | R | A | 0.01 | unsigned short int |  | 2 | 2
0003 | Frequency | R | Hz | 0.01 | unsigned short int |  | 2 | 3
0004 | Thd-V | R | % | 0.1 | unsigned short int |  | 2 | 4 |  | High Byte
0005 | Thd-I | R | % | 0.1 | unsigned short int |  | 2 | 5 |  | bit15 | bit14 | bit13 | bit12 | bit11 | bit10 | bit9 | bit8
0006 | Cos | R | - | 0.01 | short int | neg => capacitive | 2 | 6 |  | Reserved
0007 | PF | R |  | 0.01 | short int |  | 2 | 7
0008 | Active Power | R | W | 0.1 | short int | neg => export | 2 | 8 |  | Low Byte
0009 | Reactive Power | R | VAr | 0.1 | short int | neg => capacitive | 2 | 9 |  | bit7 | bit6 | bit5 | bit4 | bit3 | bit2 | bit1 | bit0
[6 empty] | Total Registers = 10 |  |  | Steps: | Reserved |  |  | 5th | 4th | 3rd | 2nd | 1st
Cap Bank Status
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
000A | cap in use status | R | - | 1 | unsigned short int |  | 2 | 10
000B | faulty cap status | R |  | 1 | unsigned short int |  | 2 | 11
000C | cap operated more than 35k hrs status | R |  | 1 | unsigned short int |  | 2 | 12
000D | 1st general status | R |  | 1 | unsigned short int |  | 2 | 13 |  | 1st General Status High Byte
000E | 2nd general status | R |  | 1 | unsigned short int | Reserved | 2 | 14 |  | bit15 | bit14 | bit13 | bit12 | bit11 | bit10 | bit9 | bit8
000F | 3rd general status | R |  | 1 | unsigned short int |  | 2 | 15 |  | Alarm Flag
[6 empty] | Total Registers = 6 |  |  |  | overLoad | - | Frequency Out of Range | under Voltage | over Compensate | under Compensate | thd-V Limit High | over Voltage
Voltage Harmonic Spectrum Parameter
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec) |  | 1st General Status Low Byte
0010 | Reserved | R | - |  | unsigned short int |  | 2 | 16 |  | bit7 | bit6 | bit5 | bit4 | bit3 | bit2 | bit1 | bit0
0011 | V Spectrum H-order 1 | R | V | 0.1 | unsigned short int |  | 2 | 17 |  | Reserved | [5 empty] | Alarm Output | Fan Output
0012 | V Spectrum H-order 2 | R | V |  | unsigned short int |  | 2 | 18
0013 | V Spectrum H-order 3 | R | V |  | unsigned short int |  | 2 | 19 | [7 empty] | 0 = OFF, 1 = On | 0 = OFF, 1 = On
0014 | V Spectrum H-order 4 | R | V |  | unsigned short int |  | 2 | 20
0015 | V Spectrum H-order 5 | R | V |  | unsigned short int |  | 2 | 21
0016 | V Spectrum H-order 6 | R | V |  | unsigned short int |  | 2 | 22
0017 | V Spectrum H-order 7 | R | V |  | unsigned short int |  | 2 | 23
0018 | V Spectrum H-order 8 | R | V |  | unsigned short int |  | 2 | 24
0019 | V Spectrum H-order 9 | R | V |  | unsigned short int |  | 2 | 25
001A | V Spectrum H-order 10 | R | V |  | unsigned short int |  | 2 | 26
001B | V Spectrum H-order 11 | R | V |  | unsigned short int |  | 2 | 27
001C | V Spectrum H-order 12 | R | V |  | unsigned short int |  | 2 | 28
001D | V Spectrum H-order 13 | R | V |  | unsigned short int |  | 2 | 29
001E | V Spectrum H-order 14 | R | V |  | unsigned short int |  | 2 | 30
001F | V Spectrum H-order 15 | R | V |  | unsigned short int |  | 2 | 31
Total Registers = 16
Ampere Harmonic Spectrum Parameter (Secondary Value)
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0020 | Reserved | R | - |  | unsigned short int |  | 2 | 32
0021 | I Spectrum H-order 1 | R | A | 0.01 | unsigned short int |  | 2 | 33
0022 | I Spectrum H-order 2 | R | A |  | unsigned short int |  | 2 | 34
0023 | I Spectrum H-order 3 | R | A |  | unsigned short int |  | 2 | 35
0024 | I Spectrum H-order 4 | R | A |  | unsigned short int |  | 2 | 36
0025 | I Spectrum H-order 5 | R | A |  | unsigned short int |  | 2 | 37
0026 | I Spectrum H-order 6 | R | A |  | unsigned short int |  | 2 | 38
0027 | I Spectrum H-order 7 | R | A |  | unsigned short int |  | 2 | 39
0028 | I Spectrum H-order 8 | R | A |  | unsigned short int |  | 2 | 40
0029 | I Spectrum H-order 9 | R | A |  | unsigned short int |  | 2 | 41
002A | I Spectrum H-order 10 | R | A |  | unsigned short int |  | 2 | 42
002B | I Spectrum H-order 11 | R | A |  | unsigned short int |  | 2 | 43
002C | I Spectrum H-order 12 | R | A |  | unsigned short int |  | 2 | 44
002D | I Spectrum H-order 13 | R | A |  | unsigned short int |  | 2 | 45
002E | I Spectrum H-order 14 | R | A |  | unsigned short int |  | 2 | 46
002F | I Spectrum H-order 15 | R | A |  | unsigned short int |  | 2 | 47
Total Registers = 16
Cap Bank Utilization Hours
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0030 | k1 cap hours | R/W | sec | 8 | unsigned short int |  | 4 | 48
0032 | k2 cap hours | R/W | sec |  | unsigned short int |  | 4 | 50
0034 | k3 cap hours | R/W | sec |  | unsigned short int |  | 4 | 52
0036 | k4 cap hours | R/W | sec |  | unsigned short int |  | 4 | 54
0038 | k5 cap hours | R/W | sec |  | unsigned short int |  | 4 | 56
003A | Reserved | R/W | - |  | unsigned short int |  | 4 | 58
003C |  | R/W |  |  | unsigned short int |  | 4 | 60
003E |  | R/W |  |  | unsigned short int |  | 4 | 62
0040 |  | R/W |  |  | unsigned short int |  | 4 | 64
0042 |  | R/W |  |  | unsigned short int |  | 4 | 66
0044 |  | R/W |  |  | unsigned short int |  | 4 | 68
0046 |  | R/W |  |  | unsigned short int |  | 4 | 70
0048 |  | R/W |  |  | unsigned short int |  | 4 | 72
004A |  | R/W |  |  | unsigned short int |  | 4 | 74
Total Registers = 28
Cap Bank Switching Count
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
004C | k1 cap switched count | R/W | - |  | unsigned short int |  | 2 | 76
004D | k2 cap switched count | R/W |  |  | unsigned short int |  | 2 | 77
004E | k3 cap switched count | R/W |  |  | unsigned short int |  | 2 | 78
004F | k4 cap switched count | R/W |  |  | unsigned short int |  | 2 | 79
0050 | k5 cap switched count | R/W |  |  | unsigned short int |  | 2 | 80
0051 | Reserved | R/W |  |  | unsigned short int |  | 2 | 81
0052 |  | R/W |  |  | unsigned short int |  | 2 | 82
0053 |  | R/W |  |  | unsigned short int |  | 2 | 83
0054 |  | R/W |  |  | unsigned short int |  | 2 | 84
0055 |  | R/W |  |  | unsigned short int |  | 2 | 85
0056 |  | R/W |  |  | unsigned short int |  | 2 | 86
0057 |  | R/W |  |  | unsigned short int |  | 2 | 87
0058 |  | R/W |  |  | unsigned short int |  | 2 | 88
0059 |  | R/W |  |  | unsigned short int |  | 2 | 89
Total Registers = 14
Cap Bank 1ph Secondary Value
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
005A | k1 cap secondary Var | R | VAr | 0.1 | unsigned short int |  | 2 | 90
005B | k2 cap secondary Var | R | VAr |  | unsigned short int |  | 2 | 91
005C | k3 cap secondary Var | R | VAr |  | unsigned short int |  | 2 | 92
005D | k4 cap secondary Var | R | VAr |  | unsigned short int |  | 2 | 93
005E | k5 cap secondary Var | R | VAr |  | unsigned short int |  | 2 | 94
005F | Reserved | R | - |  | unsigned short int |  | 2 | 95
0060 |  | R |  |  | unsigned short int |  | 2 | 96
0061 |  | R |  |  | unsigned short int |  | 2 | 97
0062 |  | R |  |  | unsigned short int |  | 2 | 98
0063 |  | R |  |  | unsigned short int |  | 2 | 99
0064 |  | R |  |  | unsigned short int |  | 2 | 100
0065 |  | R |  |  | unsigned short int |  | 2 | 101
0066 |  | R |  |  | unsigned short int |  | 2 | 102
0067 |  | R |  |  | unsigned short int |  | 2 | 103
Total Registers = 14
Cap Bank C/K ratio
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Comment | Reg Byte Count | Reg Addr (Dec)
0068 | k1 cap c/k ratio | R | - | 0.1 | unsigned short int |  | 2 | 104
0069 | k2 cap c/k ratio | R |  |  | unsigned short int |  | 2 | 105
006A | k3 cap c/k ratio | R |  |  | unsigned short int |  | 2 | 106
006B | k4 cap c/k ratio | R |  |  | unsigned short int |  | 2 | 107
006C | k5 cap c/k ratio | R |  |  | unsigned short int |  | 2 | 108
006D | Reserved | R |  | - | unsigned short int |  | 2 | 109
006E |  | R |  |  | unsigned short int |  | 2 | 110
006F |  | R |  |  | unsigned short int |  | 2 | 111
0070 |  | R |  |  | unsigned short int |  | 2 | 112
0071 |  | R |  |  | unsigned short int |  | 2 | 113
0072 |  | R |  |  | unsigned short int |  | 2 | 114
0073 |  | R |  |  | unsigned short int |  | 2 | 115
0074 |  | R |  |  | unsigned short int |  | 2 | 116
0075 |  | R |  |  | unsigned short int |  | 2 | 117
Total Registers = 14
Setting Parameter
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Data Value | Reg Byte Count | Reg Addr (Dec)
0F00 | model | R | - |  | unsigned short int | fixed 0x2105 | 2 | 3840
0F01 | firmware Ver, Map Ver | R | - | 0.01 | unsigned short int | 100, 100 | 2 | 3841
0F02 | C/K | R | - | 0.01 | unsigned short int | Auto = 0 or 1 ~ 80 | 2 | 3842
0F03 | target cos | R | - | 0.01 | short int | 85 ~ 99 ind, 100, 99 ~ 90 cap (neg) | 2 | 3843
0F04 | no.connected steps | R | - | 1 | unsigned short int | 1 ~ 5 | 2 | 3844
0F05 | switching program | R | - | 1 | unsigned short int | Auto = 0, P-0 = 1, P-1 = 2, … , P-7 = 8 | 2 | 3845
0F06 | switching on time | R | sec | 1 | unsigned short int | 1 ~ 250 | 2 | 3846
0F07 | switching off time | R | sec | 1 | unsigned short int | 1 ~ 250 | 2 | 3847
0F08 | reconnection time | R | sec | 5 | unsigned short int | OFF = 0 or 1 ~ 180 | 2 | 3848
0F09 | over voltage setting | R | V | 1 | unsigned short int | OFF = 0 or 200 ~ 260 | 2 | 3849
0F0A | thd-V setting | R | % | 1 | unsigned short int | OFF = 0 or 3 ~ 10 | 2 | 3850
0F0B | operation hour | R | min | 1 | unsigned int |  | 4 | 3851
0F0D | 1st general setting | R | - | 1 | unsigned short int |  | 2 | 3853
0F0E | 2nd general setting | R |  | 1 | unsigned short int |  | 2 | 3854
Total Registers = 15
2nd General Setting High Byte
| bit15 | bit14 | bit13 | bit12 | bit11 | bit10 | bit9 | bit8
Empty
-
2nd General Setting Low Byte
| bit7 | bit6 | bit5 | bit4 | bit3 | bit2 | bit1 | bit0
| Empty | Baud Rate |  |  | Parity |  | Plug-in Module
| - | 000 = 300, 001 = 600 010 = 1200, 011 = 2400 100 = 4800, 101 = 9600 110 = 19200, 111 = 28800 |  |  | 00 = none, 01 = odd, 10 = even |  | 00 = none, 01 = A-01s
1st General Setting High Byte
| bit15 | bit14 | bit13 | bit12 | bit11 | bit10 | bit9 | bit8
| Empty |  |  | Fan Duty | Network Type | Static Duty Interval
| - |  |  | 0 = Auto, 1 = Follow Steps | 0 = P-n, 1 = P-P | 000 = OFF, 001 = 10 mins, 010 = 15mins 011 = 20mins, 100 = 30mins 101 = 60mins, 110 = 90mins, 111 = 120mins
1st General Setting Low Byte
| bit7 | bit6 | bit5 | bit4 | bit3 | bit2 | bit1 | bit0
| Keypad Lock | Output Selection | C.T. Polarity Selection |  | Frequency Selection |  | Cap Bank Protection
| 0 = OFF, 1 = On | 0 = Fan, 1 = Alarm | 00 = Auto, 01 = Forward, 10 = Reverse |  | 00 = Auto, 01 = 50Hz, 10 = 60Hz |  | 00 = OFF, 01 = overVoltage, 10 = thd-V, 11 = ALL
Voltage Waveform
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Data Value | Reg Byte Count | Reg Addr (Dec)
0100 | V data pt <1:0> | R | - | 1 | short int |  | 2 | 256
… | … (up to) | R |  | 1 | short int |  | … | …
011F | V data pt <64:63> | R |  | 1 | short int |  | 2 | 287
Total Registers = 32
Ampere Waveform
Reg Addr (Hex) | Register | (R/W) | Unit | Multiplier | Format | Data Value | Reg Byte Count | Reg Addr (Dec)
0200 | I data pt <1:0> | R | - | 1 | short int |  | 2 | 512
… | … (up to) | R |  | 1 | short int |  | … | …
021F | I data pt <64:63> | R |  | 1 | short int |  | 2 | 543
Total Registers = 32