## Caps & Harmonics
Harmonic Simulation
Capacitor & Reactor Rating Input |  |  |  |  | Computed Values
|  | Cap Size : | 50 | kVar |  | C | = | 262.0 | uF x3 | computed from rated capacitor
|  | Cap V rating : | 450 | V |  | L | = | 0.0000 | mH | computed from rated capacitor & reactor
|  | Cap Freq rating : | 50 | Hz | Icap (rated) |  | = | 64.2 | A | rated current of capacitor
|  | Reactor Rating | 0 | % |  | F [res] | = | --- | Hz | resonance frequency for rated cap & reactor
Network Phase - Phase Value Input | [5 empty] | Irms (50Hz) | = | 59.2 | A | 1st harmonic ampere of capacitor
|  | V_1st Harmonic : | 415 | V |  | Irms (550Hz) | = | 31.4 | A | nth harmonic ampere of capacitor
|  | V_1st Freq : | 50 | Hz |  | Irms eff | = | 67.0 | A | total rms ampere of capacitor
[6 empty] | Vrms eff | = | 415.5 | V | effective rms voltage value of network
|  | V_nth Harmonic : | 20 | V |  | V[L] 1st rms | = | 0.0 | V | 1st harmonic voltage across reactor
|  | V_nth angle : | 0 | o |  | V[L] nth rms | = | 0.0 | V | nth harmonic voltage across reactor
|  | V_nth Freq : | 550 | Hz |  | V[L] eff rms | = | 0.0 | V | effective rms voltage across reactor
[6 empty] | V[C] 1st rms | = | 415.0 | V | 1st harmonic P-P rms voltage across capacitor
[6 empty] | V[C] nth rms | = | 20.0 | V | nth harmonic P-P rms voltage across capacitor
| Warning |  |  |  |  | V[C] eff rms | = | 415.5 | V | effective P-P rms voltage across capacitor
[6 empty] | Q eff | = | 41.4 | kVar | effective kVar of capacitor
| Exceeded Icap [rated] ! |  |  |  |  | THD-V | = | 4.8 | % | THD Voltage (reference to Vrms eff)
[6 empty] | THD-I | = | 46.8 | % | THD Current (reference to Irms eff)
Power Factor Controller
Power Quality Analyzer
Protection Relay

## Computation (hidden)
| V1 pk | 338.85 |  |  | C rated | 50000 | Var
| Vn pk | 16.33 |  |  | V rated | 450 | Vac
| v1 | 314.16 |  |  | F rated | 50 | Hz
| vn | 3455.75 |  |  | L (reactor) | 0 | %
| Z1[LC] | -4.05j
| Zn[LC] | -0.368181818181818j |  |  | C (Farad) | 0.0007859503363
| Z1[L] | 0 |  |  | L (Henry) | 0
| Zn[L] | 0
| Z1[C] | -4.05j
| Zn[C] | -0.368181818181818j
[12 empty] | Voltage across Reactor |  |  | Voltage @ Capacitor
|  | 415.5 | 67.0 | 415.0 |  | 20.0 |  | 59.2 |  | 31.4 |  | 0.0 | 0.0 | 0.0 | 415.0 | 20.0 | 415.5 | 0.0 | 13812.8
Spl | 1.40625 | Vrms | Irms | V1 rms |  | Vn rms |  | I1 rms |  | In rms |  | V1L rms | VnL rms | VL rms | V1c rms | Vnc rms | Vc rms | P rms | Q rms
| Angle_L1 | real | real | real | im | real | im | real | im | real | im | real | real | real | real | real | real | real | real
0 | 0 | 355.2 | 0.0 | 338.85 | 0.00 | 16.33 | 0.00 | 0 | 83.66569903 | 0 | 44.35290069 | 0.00 | 0.00 | 0.00 | 338.8 | 16.3 | 355.2 | 0.0 | 0.0
1 | 1.406 | 354.5 | -13.9 | 338.74 | 8.32 | 15.74 | 4.36 | -2.05325904 | 83.64050049 | -11.82948445 | 42.74626414 | 0.00 | 0.00 | 0.00 | 338.7 | 15.7 | 354.5 | -4921.2 | 55.0
2 | 2.813 | 352.4 | -26.9 | 338.44 | 16.63 | 14.01 | 8.40 | -4.105281273 | 83.56492003 | -22.80194796 | 38.04275186 | 0.00 | 0.00 | 0.00 | 338.4 | 14.0 | 352.4 | -9483.3 | 221.5
3 | 4.219 | 349.2 | -38.3 | 337.93 | 24.93 | 11.26 | 11.83 | -6.154830638 | 83.4390032 | -32.12245895 | 30.5831233 | 0.00 | 0.00 | 0.00 | 337.9 | 11.3 | 349.2 | -13366.0 | 501.4
4 | 5.625 | 344.9 | -47.3 | 337.21 | 33.21 | 7.70 | 14.40 | -8.200672563 | 83.26282582 | -39.11576626 | 20.90781266 | 0.00 | 0.00 | 0.00 | 337.2 | 7.7 | 344.9 | -16320.0 | 890.1
5 | 7.031 | 339.9 | -53.5 | 336.30 | 41.48 | 3.58 | 15.93 | -10.24157471 | 83.03649404 | -43.27521968 | 9.717775546 | 0.00 | 0.00 | 0.00 | 336.3 | 3.6 | 339.9 | -18189.1 | 1367.1
6 | 8.438 | 334.4 | -56.6 | 335.18 | 49.72 | -0.80 | 16.31 | -12.27630771 | 82.76014417 | -44.29947568 | -2.176293687 | 0.00 | 0.00 | 0.00 | 335.2 | -0.8 | 334.4 | -18917.7 | 1890.1
7 | 9.844 | 328.7 | -56.4 | 333.86 | 57.93 | -5.12 | 15.51 | -14.30364593 | 82.43394269 | -42.1143291 | -13.91269508 | 0.00 | 0.00 | 0.00 | 333.9 | -5.1 | 328.7 | -18546.6 | 2393.5
8 | 11.250 | 323.3 | -53.2 | 332.34 | 66.11 | -9.07 | 13.58 | -16.32236817 | 82.05808609 | -36.87808914 | -24.64115137 | 0.00 | 0.00 | 0.00 | 332.3 | -9.1 | 323.3 | -17197.7 | 2794.5
9 | 12.656 | 318.2 | -47.3 | 330.61 | 74.24 | -12.37 | 10.67 | -18.33125842 | 81.63280076 | -28.97011024 | -33.58440877 | 0.00 | 0.00 | 0.00 | 330.6 | -12.4 | 318.2 | -15053.6 | 3007.2
10 | 14.063 | 313.9 | -39.3 | 328.69 | 82.33 | -14.76 | 6.98 | -20.3291066 | 81.15834288 | -18.9633086 | -40.09454734 | 0.00 | 0.00 | 0.00 | 328.7 | -14.8 | 313.9 | -12335.0 | 2960.7
11 | 15.469 | 310.5 | -29.9 | 326.57 | 90.37 | -16.09 | 2.79 | -22.3147093 | 80.63499826 | -7.582655674 | -43.69992143 | 0.00 | 0.00 | 0.00 | 326.6 | -16.1 | 310.5 | -9282.6 | 2618.5
12 | 16.875 | 308.0 | -19.9 | 324.26 | 98.36 | -16.25 | -1.60 | -24.28687044 | 80.06308212 | 4.347344491 | -44.13932935 | 0.00 | 0.00 | 0.00 | 324.3 | -16.3 | 308.0 | -6141.5 | 1993.2
13 | 18.281 | 306.5 | -10.3 | 321.74 | 106.29 | -15.24 | -5.88 | -26.24440208 | 79.44293898 | 15.96238882 | -41.38093695 | 0.00 | 0.00 | 0.00 | 321.7 | -15.2 | 306.5 | -3151.5 | 1153.3
14 | 19.688 | 305.9 | -1.8 | 319.04 | 114.15 | -13.12 | -9.73 | -28.18612508 | 78.77494238 | 26.42099209 | -35.62458388 | 0.00 | 0.00 | 0.00 | 319.0 | -13.1 | 305.9 | -540.0 | 218.7
15 | 21.094 | 306.1 | 4.9 | 316.14 | 121.95 | -10.05 | -12.87 | -30.11086981 | 78.05949471 | 34.96545082 | -27.28730564 | 0.00 | 0.00 | 0.00 | 316.1 | -10.0 | 306.1 | 1486.0 | -654.5
16 | 22.500 | 306.8 | 9.0 | 313.05 | 129.67 | -6.25 | -15.09 | -32.01747688 | 77.29702691 | 40.97673716 | -16.97312027 | 0.00 | 0.00 | 0.00 | 313.1 | -6.2 | 306.8 | 2748.7 | -1296.9
17 | 23.906 | 307.8 | 10.1 | 309.78 | 137.31 | -2.00 | -16.21 | -33.90479781 | 76.48799827 | 44.01934624 | -5.429268521 | 0.00 | 0.00 | 0.00 | 309.8 | -2.0 | 307.8 | 3113.0 | -1552.8
18 | 25.313 | 308.7 | 8.1 | 306.31 | 144.88 | 2.40 | -16.15 | -35.77169577 | 75.63289613 | 43.87284751 | 6.507922162 | 0.00 | 0.00 | 0.00 | 306.3 | 2.4 | 308.7 | 2500.9 | -1304.5
19 | 26.719 | 309.3 | 2.9 | 302.67 | 152.35 | 6.62 | -14.93 | -37.61704619 | 74.73223555 | 40.54785451 | 17.97362776 | 0.00 | 0.00 | 0.00 | 302.7 | 6.6 | 309.3 | 906.4 | -490.3
20 | 28.125 | 309.2 | -5.2 | 298.84 | 159.73 | 10.36 | -12.62 | -39.43973751 | 73.78655907 | 34.28525587 | 28.13718233 | 0.00 | 0.00 | 0.00 | 298.8 | 10.4 | 309.2 | -1593.7 | 888.4
21 | 29.531 | 308.2 | -15.7 | 294.83 | 167.02 | 13.35 | -9.40 | -41.23867181 | 72.79643633 | 25.53876353 | 36.26225803 | 0.00 | 0.00 | 0.00 | 294.8 | 13.4 | 308.2 | -4838.3 | 2769.8
22 | 30.938 | 306.0 | -28.1 | 290.64 | 174.20 | 15.38 | -5.50 | -43.01276547 | 71.76246374 | 14.94204221 | 41.76021042 | 0.00 | 0.00 | 0.00 | 290.6 | 15.4 | 306.0 | -8590.0 | 5044.4
23 | 32.344 | 302.6 | -41.5 | 286.28 | 181.28 | 16.29 | -1.20 | -44.76094985 | 70.68526412 | 3.262801784 | 44.23272459 | 0.00 | 0.00 | 0.00 | 286.3 | 16.3 | 302.6 | -12555.7 | 7572.7
24 | 33.750 | 297.8 | -55.1 | 281.74 | 188.25 | 16.02 | 3.19 | -46.48217191 | 69.56548634 | -8.652821678 | 43.50067214 | 0.00 | 0.00 | 0.00 | 281.7 | 16.0 | 297.8 | -16416.8 | 10203.7
25 | 35.156 | 291.6 | -68.1 | 277.04 | 195.11 | 14.59 | 7.34 | -48.17539484 | 68.40380491 | -19.94156665 | 39.61708873 | 0.00 | 0.00 | 0.00 | 277.0 | 14.6 | 291.6 | -19864.4 | 12790.2
26 | 36.563 | 284.3 | -79.6 | 272.16 | 201.85 | 12.10 | 10.97 | -49.83959872 | 67.20091959 | -29.78558763 | 32.86333168 | 0.00 | 0.00 | 0.00 | 272.2 | 12.1 | 284.3 | -22634.5 | 15199.2
27 | 37.969 | 275.9 | -88.9 | 267.13 | 208.47 | 8.74 | 13.80 | -51.47378109 | 65.95755495 | -37.47170628 | 23.72869631 | 0.00 | 0.00 | 0.00 | 267.1 | 8.7 | 275.9 | -24536.9 | 17315.2
28 | 39.375 | 266.7 | -95.5 | 261.93 | 214.96 | 4.74 | 15.63 | -53.07695758 | 64.67445994 | -42.44307968 | 12.87496746 | 0.00 | 0.00 | 0.00 | 261.9 | 4.7 | 266.7 | -25472.5 | 19040.5
29 | 40.781 | 257.0 | -99.0 | 256.58 | 221.33 | 0.40 | 16.33 | -54.6481625 | 63.35240746 | -44.33954243 | 1.088474672 | 0.00 | 0.00 | 0.00 | 256.6 | 0.4 | 257.0 | -25437.7 | 20292.5
30 | 42.188 | 247.1 | -99.2 | 251.07 | 227.56 | -3.97 | 15.84 | -56.1864494 | 61.99219385 | -43.02369984 | -10.77687579 | 0.00 | 0.00 | 0.00 | 251.1 | -4.0 | 247.1 | -24514.9 | 21004.2
31 | 43.594 | 237.4 | -96.3 | 245.41 | 233.65 | -8.05 | 14.21 | -57.69089169 | 60.59463847 | -38.59088191 | -21.86146457 | 0.00 | 0.00 | 0.00 | 245.4 | -8.0 | 237.4 | -22853.4 | 21128.0
32 | 45.000 | 228.1 | -90.5 | 239.60 | 239.60 | -11.55 | 11.55 | -59.16058314 | 59.16058314 | -31.36223684 | -31.36223684 | 0.00 | 0.00 | 0.00 | 239.6 | -11.5 | 228.1 | -20644.0 | 20644.0
33 | 46.406 | 219.4 | -82.5 | 233.65 | 245.41 | -14.21 | 8.05 | -60.59463847 | 57.69089169 | -21.86146457 | -38.59088191 | 0.00 | 0.00 | 0.00 | 233.6 | -14.2 | 219.4 | -18094.1 | 19571.7
34 | 47.813 | 211.7 | -72.8 | 227.56 | 251.07 | -15.84 | 3.97 | -61.99219385 | 56.1864494 | -10.77687579 | -43.02369984 | 0.00 | 0.00 | 0.00 | 227.6 | -15.8 | 211.7 | -15406.3 | 17981.3
35 | 49.219 | 205.0 | -62.3 | 221.33 | 256.58 | -16.33 | -0.40 | -63.35240746 | 54.6481625 | 1.088474672 | -44.33954243 | 0.00 | 0.00 | 0.00 | 221.3 | -16.3 | 205.0 | -12764.1 | 16000.5
36 | 50.625 | 199.3 | -51.8 | 214.96 | 261.93 | -15.63 | -4.74 | -64.67445994 | 53.07695758 | 12.87496746 | -42.44307968 | 0.00 | 0.00 | 0.00 | 215.0 | -15.6 | 199.3 | -10325.4 | 13813.5
37 | 52.031 | 194.7 | -42.2 | 208.47 | 267.13 | -13.80 | -8.74 | -65.95755495 | 51.47378109 | 23.72869631 | -37.47170628 | 0.00 | 0.00 | 0.00 | 208.5 | -13.8 | 194.7 | -8220.8 | 11649.4
38 | 53.438 | 190.9 | -34.3 | 201.85 | 272.16 | -10.97 | -12.10 | -67.20091959 | 49.83959872 | 32.86333168 | -29.78558763 | 0.00 | 0.00 | 0.00 | 201.9 | -11.0 | 190.9 | -6554.5 | 9760.9
39 | 54.844 | 187.8 | -28.8 | 195.11 | 277.04 | -7.34 | -14.59 | -68.40380491 | 48.17539484 | 39.61708873 | -19.94156665 | 0.00 | 0.00 | 0.00 | 195.1 | -7.3 | 187.8 | -5405.2 | 8394.8
40 | 56.250 | 185.1 | -26.1 | 188.25 | 281.74 | -3.19 | -16.02 | -69.56548634 | 46.48217191 | 43.50067214 | -8.652821678 | 0.00 | 0.00 | 0.00 | 188.3 | -3.2 | 185.1 | -4823.7 | 7761.0
41 | 57.656 | 182.5 | -26.5 | 181.28 | 286.28 | 1.20 | -16.29 | -70.68526412 | 44.76094985 | 44.23272459 | 3.262801784 | 0.00 | 0.00 | 0.00 | 181.3 | 1.2 | 182.5 | -4827.1 | 8003.5
42 | 59.063 | 179.7 | -30.0 | 174.20 | 290.64 | 5.50 | -15.38 | -71.76246374 | 43.01276547 | 41.76021042 | 14.94204221 | 0.00 | 0.00 | 0.00 | 174.2 | 5.5 | 179.7 | -5391.5 | 9181.1
43 | 60.469 | 176.4 | -36.5 | 167.02 | 294.83 | 9.40 | -13.35 | -72.79643633 | 41.23867181 | 36.26225803 | 25.53876353 | 0.00 | 0.00 | 0.00 | 167.0 | 9.4 | 176.4 | -6445.3 | 11259.0
44 | 61.875 | 172.4 | -45.6 | 159.73 | 298.84 | 12.62 | -10.36 | -73.78655907 | 39.43973751 | 28.13718233 | 34.28525587 | 0.00 | 0.00 | 0.00 | 159.7 | 12.6 | 172.4 | -7867.9 | 14114.6
45 | 63.281 | 167.3 | -56.8 | 152.35 | 302.67 | 14.93 | -6.62 | -74.73223555 | 37.61704619 | 17.97362776 | 40.54785451 | 0.00 | 0.00 | 0.00 | 152.3 | 14.9 | 167.3 | -9494.5 | 17554.5
46 | 64.688 | 161.0 | -69.1 | 144.88 | 306.31 | 16.15 | -2.40 | -75.63289613 | 35.77169577 | 6.507922162 | 43.87284751 | 0.00 | 0.00 | 0.00 | 144.9 | 16.2 | 161.0 | -11131.1 | 21339.5
47 | 66.094 | 153.5 | -81.9 | 137.31 | 309.78 | 16.21 | 2.00 | -76.48799827 | 33.90479781 | -5.429268521 | 44.01934624 | 0.00 | 0.00 | 0.00 | 137.3 | 16.2 | 153.5 | -12576.1 | 25212.3
48 | 67.500 | 144.8 | -94.3 | 129.67 | 313.05 | 15.09 | 6.25 | -77.29702691 | 32.01747688 | -16.97312027 | 40.97673716 | 0.00 | 0.00 | 0.00 | 129.7 | 15.1 | 144.8 | -13646.3 | 28922.4
49 | 68.906 | 134.8 | -105.3 | 121.95 | 316.14 | 12.87 | 10.05 | -78.05949471 | 30.11086981 | -27.28730564 | 34.96545082 | 0.00 | 0.00 | 0.00 | 121.9 | 12.9 | 134.8 | -14203.1 | 32246.1
50 | 70.313 | 123.9 | -114.4 | 114.15 | 319.04 | 9.73 | 13.12 | -78.77494238 | 28.18612508 | -35.62458388 | 26.42099209 | 0.00 | 0.00 | 0.00 | 114.2 | 9.7 | 123.9 | -14172.0 | 34997.4
51 | 71.719 | 112.2 | -120.8 | 106.29 | 321.74 | 5.88 | 15.24 | -79.44293898 | 26.24440208 | -41.38093695 | 15.96238882 | 0.00 | 0.00 | 0.00 | 106.3 | 5.9 | 112.2 | -13552.4 | 37033.5
52 | 73.125 | 100.0 | -124.2 | 98.36 | 324.26 | 1.60 | 16.25 | -80.06308212 | 24.28687044 | -44.13932935 | 4.347344491 | 0.00 | 0.00 | 0.00 | 98.4 | 1.6 | 100.0 | -12415.6 | 38254.9
53 | 74.531 | 87.6 | -124.3 | 90.37 | 326.57 | -2.79 | 16.09 | -80.63499826 | 22.3147093 | -43.69992143 | -7.582655674 | 0.00 | 0.00 | 0.00 | 90.4 | -2.8 | 87.6 | -10889.6 | 38603.8
54 | 75.938 | 75.4 | -121.3 | 82.33 | 328.69 | -6.98 | 14.76 | -81.15834288 | 20.3291066 | -40.09454734 | -18.9633086 | 0.00 | 0.00 | 0.00 | 82.3 | -7.0 | 75.4 | -9136.5 | 38064.8
55 | 77.344 | 63.6 | -115.2 | 74.24 | 330.61 | -10.67 | 12.37 | -81.63280076 | 18.33125842 | -33.58440877 | -28.97011024 | 0.00 | 0.00 | 0.00 | 74.2 | -10.7 | 63.6 | -7325.0 | 36667.6
56 | 78.750 | 52.5 | -106.7 | 66.11 | 332.34 | -13.58 | 9.07 | -82.05808609 | 16.32236817 | -24.64115137 | -36.87808914 | 0.00 | 0.00 | 0.00 | 66.1 | -13.6 | 52.5 | -5604.7 | 34491.9
57 | 80.156 | 42.4 | -96.3 | 57.93 | 333.86 | -15.51 | 5.12 | -82.43394269 | 14.30364593 | -13.91269508 | -42.1143291 | 0.00 | 0.00 | 0.00 | 57.9 | -15.5 | 42.4 | -4087.4 | 31672.5
58 | 81.563 | 33.4 | -84.9 | 49.72 | 335.18 | -16.31 | 0.80 | -82.76014417 | 12.27630771 | -2.176293687 | -44.29947568 | 0.00 | 0.00 | 0.00 | 49.7 | -16.3 | 33.4 | -2837.6 | 28400.8
59 | 82.969 | 25.5 | -73.3 | 41.48 | 336.30 | -15.93 | -3.58 | -83.03649404 | 10.24157471 | 9.717775546 | -43.27521968 | 0.00 | 0.00 | 0.00 | 41.5 | -15.9 | 25.5 | -1872.9 | 24919.3
60 | 84.375 | 18.8 | -62.4 | 33.21 | 337.21 | -14.40 | -7.70 | -83.26282582 | 8.200672563 | 20.90781266 | -39.11576626 | 0.00 | 0.00 | 0.00 | 33.2 | -14.4 | 18.8 | -1173.0 | 21507.0
61 | 85.781 | 13.1 | -52.9 | 24.93 | 337.93 | -11.83 | -11.26 | -83.4390032 | 6.154830638 | 30.5831233 | -32.12245895 | 0.00 | 0.00 | 0.00 | 24.9 | -11.8 | 13.1 | -692.4 | 18456.6
62 | 87.188 | 8.2 | -45.5 | 16.63 | 338.44 | -8.40 | -14.01 | -83.56492003 | 4.105281273 | 38.04275186 | -22.80194796 | 0.00 | 0.00 | 0.00 | 16.6 | -8.4 | 8.2 | -374.7 | 16044.0
63 | 88.594 | 4.0 | -40.9 | 8.32 | 338.74 | -4.36 | -15.74 | -83.64050049 | 2.05325904 | 42.74626414 | -11.82948445 | 0.00 | 0.00 | 0.00 | 8.3 | -4.4 | 4.0 | -162.0 | 14496.3
64 | 90.000 | 0.0 | -39.3 | 0.00 | 338.85 | 0.00 | -16.33 | -83.66569903 | 0 | 44.35290069 | 0 | 0.00 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 | 0.0 | 13963.0
65 | 91.406 | -4.0 | -40.9 | -8.32 | 338.74 | 4.36 | -15.74 | -83.64050049 | -2.05325904 | 42.74626414 | 11.82948445 | 0.00 | 0.00 | 0.00 | -8.3 | 4.4 | -4.0 | 162.0 | 14496.3
66 | 92.813 | -8.2 | -45.5 | -16.63 | 338.44 | 8.40 | -14.01 | -83.56492003 | -4.105281273 | 38.04275186 | 22.80194796 | 0.00 | 0.00 | 0.00 | -16.6 | 8.4 | -8.2 | 374.7 | 16044.0
67 | 94.219 | -13.1 | -52.9 | -24.93 | 337.93 | 11.83 | -11.26 | -83.4390032 | -6.154830638 | 30.5831233 | 32.12245895 | 0.00 | 0.00 | 0.00 | -24.9 | 11.8 | -13.1 | 692.4 | 18456.6
68 | 95.625 | -18.8 | -62.4 | -33.21 | 337.21 | 14.40 | -7.70 | -83.26282582 | -8.200672563 | 20.90781266 | 39.11576626 | 0.00 | 0.00 | 0.00 | -33.2 | 14.4 | -18.8 | 1173.0 | 21507.0
69 | 97.031 | -25.5 | -73.3 | -41.48 | 336.30 | 15.93 | -3.58 | -83.03649404 | -10.24157471 | 9.717775546 | 43.27521968 | 0.00 | 0.00 | 0.00 | -41.5 | 15.9 | -25.5 | 1872.9 | 24919.3
70 | 98.438 | -33.4 | -84.9 | -49.72 | 335.18 | 16.31 | 0.80 | -82.76014417 | -12.27630771 | -2.176293687 | 44.29947568 | 0.00 | 0.00 | 0.00 | -49.7 | 16.3 | -33.4 | 2837.6 | 28400.8
71 | 99.844 | -42.4 | -96.3 | -57.93 | 333.86 | 15.51 | 5.12 | -82.43394269 | -14.30364593 | -13.91269508 | 42.1143291 | 0.00 | 0.00 | 0.00 | -57.9 | 15.5 | -42.4 | 4087.4 | 31672.5
72 | 101.250 | -52.5 | -106.7 | -66.11 | 332.34 | 13.58 | 9.07 | -82.05808609 | -16.32236817 | -24.64115137 | 36.87808914 | 0.00 | 0.00 | 0.00 | -66.1 | 13.6 | -52.5 | 5604.7 | 34491.9
73 | 102.656 | -63.6 | -115.2 | -74.24 | 330.61 | 10.67 | 12.37 | -81.63280076 | -18.33125842 | -33.58440877 | 28.97011024 | 0.00 | 0.00 | 0.00 | -74.2 | 10.7 | -63.6 | 7325.0 | 36667.6
74 | 104.063 | -75.4 | -121.3 | -82.33 | 328.69 | 6.98 | 14.76 | -81.15834288 | -20.3291066 | -40.09454734 | 18.9633086 | 0.00 | 0.00 | 0.00 | -82.3 | 7.0 | -75.4 | 9136.5 | 38064.8
75 | 105.469 | -87.6 | -124.3 | -90.37 | 326.57 | 2.79 | 16.09 | -80.63499826 | -22.3147093 | -43.69992143 | 7.582655674 | 0.00 | 0.00 | 0.00 | -90.4 | 2.8 | -87.6 | 10889.6 | 38603.8
76 | 106.875 | -100.0 | -124.2 | -98.36 | 324.26 | -1.60 | 16.25 | -80.06308212 | -24.28687044 | -44.13932935 | -4.347344491 | 0.00 | 0.00 | 0.00 | -98.4 | -1.6 | -100.0 | 12415.6 | 38254.9
77 | 108.281 | -112.2 | -120.8 | -106.29 | 321.74 | -5.88 | 15.24 | -79.44293898 | -26.24440208 | -41.38093695 | -15.96238882 | 0.00 | 0.00 | 0.00 | -106.3 | -5.9 | -112.2 | 13552.4 | 37033.5
78 | 109.688 | -123.9 | -114.4 | -114.15 | 319.04 | -9.73 | 13.12 | -78.77494238 | -28.18612508 | -35.62458388 | -26.42099209 | 0.00 | 0.00 | 0.00 | -114.2 | -9.7 | -123.9 | 14172.0 | 34997.4
79 | 111.094 | -134.8 | -105.3 | -121.95 | 316.14 | -12.87 | 10.05 | -78.05949471 | -30.11086981 | -27.28730564 | -34.96545082 | 0.00 | 0.00 | 0.00 | -121.9 | -12.9 | -134.8 | 14203.1 | 32246.1
80 | 112.500 | -144.8 | -94.3 | -129.67 | 313.05 | -15.09 | 6.25 | -77.29702691 | -32.01747688 | -16.97312027 | -40.97673716 | 0.00 | 0.00 | 0.00 | -129.7 | -15.1 | -144.8 | 13646.3 | 28922.4
81 | 113.906 | -153.5 | -81.9 | -137.31 | 309.78 | -16.21 | 2.00 | -76.48799827 | -33.90479781 | -5.429268521 | -44.01934624 | 0.00 | 0.00 | 0.00 | -137.3 | -16.2 | -153.5 | 12576.1 | 25212.3
82 | 115.313 | -161.0 | -69.1 | -144.88 | 306.31 | -16.15 | -2.40 | -75.63289613 | -35.77169577 | 6.507922162 | -43.87284751 | 0.00 | 0.00 | 0.00 | -144.9 | -16.2 | -161.0 | 11131.1 | 21339.5
83 | 116.719 | -167.3 | -56.8 | -152.35 | 302.67 | -14.93 | -6.62 | -74.73223555 | -37.61704619 | 17.97362776 | -40.54785451 | 0.00 | 0.00 | 0.00 | -152.3 | -14.9 | -167.3 | 9494.5 | 17554.5
84 | 118.125 | -172.4 | -45.6 | -159.73 | 298.84 | -12.62 | -10.36 | -73.78655907 | -39.43973751 | 28.13718233 | -34.28525587 | 0.00 | 0.00 | 0.00 | -159.7 | -12.6 | -172.4 | 7867.9 | 14114.6
85 | 119.531 | -176.4 | -36.5 | -167.02 | 294.83 | -9.40 | -13.35 | -72.79643633 | -41.23867181 | 36.26225803 | -25.53876353 | 0.00 | 0.00 | 0.00 | -167.0 | -9.4 | -176.4 | 6445.3 | 11259.0
86 | 120.938 | -179.7 | -30.0 | -174.20 | 290.64 | -5.50 | -15.38 | -71.76246374 | -43.01276547 | 41.76021042 | -14.94204221 | 0.00 | 0.00 | 0.00 | -174.2 | -5.5 | -179.7 | 5391.5 | 9181.1
87 | 122.344 | -182.5 | -26.5 | -181.28 | 286.28 | -1.20 | -16.29 | -70.68526412 | -44.76094985 | 44.23272459 | -3.262801784 | 0.00 | 0.00 | 0.00 | -181.3 | -1.2 | -182.5 | 4827.1 | 8003.5
88 | 123.750 | -185.1 | -26.1 | -188.25 | 281.74 | 3.19 | -16.02 | -69.56548634 | -46.48217191 | 43.50067214 | 8.652821678 | 0.00 | 0.00 | 0.00 | -188.3 | 3.2 | -185.1 | 4823.7 | 7761.0
89 | 125.156 | -187.8 | -28.8 | -195.11 | 277.04 | 7.34 | -14.59 | -68.40380491 | -48.17539484 | 39.61708873 | 19.94156665 | 0.00 | 0.00 | 0.00 | -195.1 | 7.3 | -187.8 | 5405.2 | 8394.8
90 | 126.563 | -190.9 | -34.3 | -201.85 | 272.16 | 10.97 | -12.10 | -67.20091959 | -49.83959872 | 32.86333168 | 29.78558763 | 0.00 | 0.00 | 0.00 | -201.9 | 11.0 | -190.9 | 6554.5 | 9760.9
91 | 127.969 | -194.7 | -42.2 | -208.47 | 267.13 | 13.80 | -8.74 | -65.95755495 | -51.47378109 | 23.72869631 | 37.47170628 | 0.00 | 0.00 | 0.00 | -208.5 | 13.8 | -194.7 | 8220.8 | 11649.4
92 | 129.375 | -199.3 | -51.8 | -214.96 | 261.93 | 15.63 | -4.74 | -64.67445994 | -53.07695758 | 12.87496746 | 42.44307968 | 0.00 | 0.00 | 0.00 | -215.0 | 15.6 | -199.3 | 10325.4 | 13813.5
93 | 130.781 | -205.0 | -62.3 | -221.33 | 256.58 | 16.33 | -0.40 | -63.35240746 | -54.6481625 | 1.088474672 | 44.33954243 | 0.00 | 0.00 | 0.00 | -221.3 | 16.3 | -205.0 | 12764.1 | 16000.5
94 | 132.188 | -211.7 | -72.8 | -227.56 | 251.07 | 15.84 | 3.97 | -61.99219385 | -56.1864494 | -10.77687579 | 43.02369984 | 0.00 | 0.00 | 0.00 | -227.6 | 15.8 | -211.7 | 15406.3 | 17981.3
95 | 133.594 | -219.4 | -82.5 | -233.65 | 245.41 | 14.21 | 8.05 | -60.59463847 | -57.69089169 | -21.86146457 | 38.59088191 | 0.00 | 0.00 | 0.00 | -233.6 | 14.2 | -219.4 | 18094.1 | 19571.7
96 | 135.000 | -228.1 | -90.5 | -239.60 | 239.60 | 11.55 | 11.55 | -59.16058314 | -59.16058314 | -31.36223684 | 31.36223684 | 0.00 | 0.00 | 0.00 | -239.6 | 11.5 | -228.1 | 20644.0 | 20644.0
97 | 136.406 | -237.4 | -96.3 | -245.41 | 233.65 | 8.05 | 14.21 | -57.69089169 | -60.59463847 | -38.59088191 | 21.86146457 | 0.00 | 0.00 | 0.00 | -245.4 | 8.0 | -237.4 | 22853.4 | 21128.0
98 | 137.813 | -247.1 | -99.2 | -251.07 | 227.56 | 3.97 | 15.84 | -56.1864494 | -61.99219385 | -43.02369984 | 10.77687579 | 0.00 | 0.00 | 0.00 | -251.1 | 4.0 | -247.1 | 24514.9 | 21004.2
99 | 139.219 | -257.0 | -99.0 | -256.58 | 221.33 | -0.40 | 16.33 | -54.6481625 | -63.35240746 | -44.33954243 | -1.088474672 | 0.00 | 0.00 | 0.00 | -256.6 | -0.4 | -257.0 | 25437.7 | 20292.5
100 | 140.625 | -266.7 | -95.5 | -261.93 | 214.96 | -4.74 | 15.63 | -53.07695758 | -64.67445994 | -42.44307968 | -12.87496746 | 0.00 | 0.00 | 0.00 | -261.9 | -4.7 | -266.7 | 25472.5 | 19040.5
101 | 142.031 | -275.9 | -88.9 | -267.13 | 208.47 | -8.74 | 13.80 | -51.47378109 | -65.95755495 | -37.47170628 | -23.72869631 | 0.00 | 0.00 | 0.00 | -267.1 | -8.7 | -275.9 | 24536.9 | 17315.2
102 | 143.438 | -284.3 | -79.6 | -272.16 | 201.85 | -12.10 | 10.97 | -49.83959872 | -67.20091959 | -29.78558763 | -32.86333168 | 0.00 | 0.00 | 0.00 | -272.2 | -12.1 | -284.3 | 22634.5 | 15199.2
103 | 144.844 | -291.6 | -68.1 | -277.04 | 195.11 | -14.59 | 7.34 | -48.17539484 | -68.40380491 | -19.94156665 | -39.61708873 | 0.00 | 0.00 | 0.00 | -277.0 | -14.6 | -291.6 | 19864.4 | 12790.2
104 | 146.250 | -297.8 | -55.1 | -281.74 | 188.25 | -16.02 | 3.19 | -46.48217191 | -69.56548634 | -8.652821678 | -43.50067214 | 0.00 | 0.00 | 0.00 | -281.7 | -16.0 | -297.8 | 16416.8 | 10203.7
105 | 147.656 | -302.6 | -41.5 | -286.28 | 181.28 | -16.29 | -1.20 | -44.76094985 | -70.68526412 | 3.262801784 | -44.23272459 | 0.00 | 0.00 | 0.00 | -286.3 | -16.3 | -302.6 | 12555.7 | 7572.7
106 | 149.063 | -306.0 | -28.1 | -290.64 | 174.20 | -15.38 | -5.50 | -43.01276547 | -71.76246374 | 14.94204221 | -41.76021042 | 0.00 | 0.00 | 0.00 | -290.6 | -15.4 | -306.0 | 8590.0 | 5044.4
107 | 150.469 | -308.2 | -15.7 | -294.83 | 167.02 | -13.35 | -9.40 | -41.23867181 | -72.79643633 | 25.53876353 | -36.26225803 | 0.00 | 0.00 | 0.00 | -294.8 | -13.4 | -308.2 | 4838.3 | 2769.8
108 | 151.875 | -309.2 | -5.2 | -298.84 | 159.73 | -10.36 | -12.62 | -39.43973751 | -73.78655907 | 34.28525587 | -28.13718233 | 0.00 | 0.00 | 0.00 | -298.8 | -10.4 | -309.2 | 1593.7 | 888.4
109 | 153.281 | -309.3 | 2.9 | -302.67 | 152.35 | -6.62 | -14.93 | -37.61704619 | -74.73223555 | 40.54785451 | -17.97362776 | 0.00 | 0.00 | 0.00 | -302.7 | -6.6 | -309.3 | -906.4 | -490.3
110 | 154.688 | -308.7 | 8.1 | -306.31 | 144.88 | -2.40 | -16.15 | -35.77169577 | -75.63289613 | 43.87284751 | -6.507922162 | 0.00 | 0.00 | 0.00 | -306.3 | -2.4 | -308.7 | -2500.9 | -1304.5
111 | 156.094 | -307.8 | 10.1 | -309.78 | 137.31 | 2.00 | -16.21 | -33.90479781 | -76.48799827 | 44.01934624 | 5.429268521 | 0.00 | 0.00 | 0.00 | -309.8 | 2.0 | -307.8 | -3113.0 | -1552.8
112 | 157.500 | -306.8 | 9.0 | -313.05 | 129.67 | 6.25 | -15.09 | -32.01747688 | -77.29702691 | 40.97673716 | 16.97312027 | 0.00 | 0.00 | 0.00 | -313.1 | 6.2 | -306.8 | -2748.7 | -1296.9
113 | 158.906 | -306.1 | 4.9 | -316.14 | 121.95 | 10.05 | -12.87 | -30.11086981 | -78.05949471 | 34.96545082 | 27.28730564 | 0.00 | 0.00 | 0.00 | -316.1 | 10.0 | -306.1 | -1486.0 | -654.5
114 | 160.313 | -305.9 | -1.8 | -319.04 | 114.15 | 13.12 | -9.73 | -28.18612508 | -78.77494238 | 26.42099209 | 35.62458388 | 0.00 | 0.00 | 0.00 | -319.0 | 13.1 | -305.9 | 540.0 | 218.7
115 | 161.719 | -306.5 | -10.3 | -321.74 | 106.29 | 15.24 | -5.88 | -26.24440208 | -79.44293898 | 15.96238882 | 41.38093695 | 0.00 | 0.00 | 0.00 | -321.7 | 15.2 | -306.5 | 3151.5 | 1153.3
116 | 163.125 | -308.0 | -19.9 | -324.26 | 98.36 | 16.25 | -1.60 | -24.28687044 | -80.06308212 | 4.347344491 | 44.13932935 | 0.00 | 0.00 | 0.00 | -324.3 | 16.3 | -308.0 | 6141.5 | 1993.2
117 | 164.531 | -310.5 | -29.9 | -326.57 | 90.37 | 16.09 | 2.79 | -22.3147093 | -80.63499826 | -7.582655674 | 43.69992143 | 0.00 | 0.00 | 0.00 | -326.6 | 16.1 | -310.5 | 9282.6 | 2618.5
118 | 165.938 | -313.9 | -39.3 | -328.69 | 82.33 | 14.76 | 6.98 | -20.3291066 | -81.15834288 | -18.9633086 | 40.09454734 | 0.00 | 0.00 | 0.00 | -328.7 | 14.8 | -313.9 | 12335.0 | 2960.7
119 | 167.344 | -318.2 | -47.3 | -330.61 | 74.24 | 12.37 | 10.67 | -18.33125842 | -81.63280076 | -28.97011024 | 33.58440877 | 0.00 | 0.00 | 0.00 | -330.6 | 12.4 | -318.2 | 15053.6 | 3007.2
120 | 168.750 | -323.3 | -53.2 | -332.34 | 66.11 | 9.07 | 13.58 | -16.32236817 | -82.05808609 | -36.87808914 | 24.64115137 | 0.00 | 0.00 | 0.00 | -332.3 | 9.1 | -323.3 | 17197.7 | 2794.5
121 | 170.156 | -328.7 | -56.4 | -333.86 | 57.93 | 5.12 | 15.51 | -14.30364593 | -82.43394269 | -42.1143291 | 13.91269508 | 0.00 | 0.00 | 0.00 | -333.9 | 5.1 | -328.7 | 18546.6 | 2393.5
122 | 171.563 | -334.4 | -56.6 | -335.18 | 49.72 | 0.80 | 16.31 | -12.27630771 | -82.76014417 | -44.29947568 | 2.176293687 | 0.00 | 0.00 | 0.00 | -335.2 | 0.8 | -334.4 | 18917.7 | 1890.1
123 | 172.969 | -339.9 | -53.5 | -336.30 | 41.48 | -3.58 | 15.93 | -10.24157471 | -83.03649404 | -43.27521968 | -9.717775546 | 0.00 | 0.00 | 0.00 | -336.3 | -3.6 | -339.9 | 18189.1 | 1367.1
124 | 174.375 | -344.9 | -47.3 | -337.21 | 33.21 | -7.70 | 14.40 | -8.200672563 | -83.26282582 | -39.11576626 | -20.90781266 | 0.00 | 0.00 | 0.00 | -337.2 | -7.7 | -344.9 | 16320.0 | 890.1
125 | 175.781 | -349.2 | -38.3 | -337.93 | 24.93 | -11.26 | 11.83 | -6.154830638 | -83.4390032 | -32.12245895 | -30.5831233 | 0.00 | 0.00 | 0.00 | -337.9 | -11.3 | -349.2 | 13366.0 | 501.4
126 | 177.188 | -352.4 | -26.9 | -338.44 | 16.63 | -14.01 | 8.40 | -4.105281273 | -83.56492003 | -22.80194796 | -38.04275186 | 0.00 | 0.00 | 0.00 | -338.4 | -14.0 | -352.4 | 9483.3 | 221.5
127 | 178.594 | -354.5 | -13.9 | -338.74 | 8.32 | -15.74 | 4.36 | -2.05325904 | -83.64050049 | -11.82948445 | -42.74626414 | 0.00 | 0.00 | 0.00 | -338.7 | -15.7 | -354.5 | 4921.2 | 55.0
128 | 180.000 | -355.2 | 0.0 | -338.85 | 0.00 | -16.33 | 0.00 | 0 | -83.66569903 | 0 | -44.35290069 | 0.00 | 0.00 | 0.00 | -338.8 | -16.3 | -355.2 | 0.0 | 0.0
129 | 181.406 | -354.5 | 13.9 | -338.74 | -8.32 | -15.74 | -4.36 | 2.05325904 | -83.64050049 | 11.82948445 | -42.74626414 | 0.00 | 0.00 | 0.00 | -338.7 | -15.7 | -354.5 | -4921.2 | 55.0
130 | 182.813 | -352.4 | 26.9 | -338.44 | -16.63 | -14.01 | -8.40 | 4.105281273 | -83.56492003 | 22.80194796 | -38.04275186 | 0.00 | 0.00 | 0.00 | -338.4 | -14.0 | -352.4 | -9483.3 | 221.5
131 | 184.219 | -349.2 | 38.3 | -337.93 | -24.93 | -11.26 | -11.83 | 6.154830638 | -83.4390032 | 32.12245895 | -30.5831233 | 0.00 | 0.00 | 0.00 | -337.9 | -11.3 | -349.2 | -13366.0 | 501.4
132 | 185.625 | -344.9 | 47.3 | -337.21 | -33.21 | -7.70 | -14.40 | 8.200672563 | -83.26282582 | 39.11576626 | -20.90781266 | 0.00 | 0.00 | 0.00 | -337.2 | -7.7 | -344.9 | -16320.0 | 890.1
133 | 187.031 | -339.9 | 53.5 | -336.30 | -41.48 | -3.58 | -15.93 | 10.24157471 | -83.03649404 | 43.27521968 | -9.717775546 | 0.00 | 0.00 | 0.00 | -336.3 | -3.6 | -339.9 | -18189.1 | 1367.1
134 | 188.438 | -334.4 | 56.6 | -335.18 | -49.72 | 0.80 | -16.31 | 12.27630771 | -82.76014417 | 44.29947568 | 2.176293687 | 0.00 | 0.00 | 0.00 | -335.2 | 0.8 | -334.4 | -18917.7 | 1890.1
135 | 189.844 | -328.7 | 56.4 | -333.86 | -57.93 | 5.12 | -15.51 | 14.30364593 | -82.43394269 | 42.1143291 | 13.91269508 | 0.00 | 0.00 | 0.00 | -333.9 | 5.1 | -328.7 | -18546.6 | 2393.5
136 | 191.250 | -323.3 | 53.2 | -332.34 | -66.11 | 9.07 | -13.58 | 16.32236817 | -82.05808609 | 36.87808914 | 24.64115137 | 0.00 | 0.00 | 0.00 | -332.3 | 9.1 | -323.3 | -17197.7 | 2794.5
137 | 192.656 | -318.2 | 47.3 | -330.61 | -74.24 | 12.37 | -10.67 | 18.33125842 | -81.63280076 | 28.97011024 | 33.58440877 | 0.00 | 0.00 | 0.00 | -330.6 | 12.4 | -318.2 | -15053.6 | 3007.2
138 | 194.063 | -313.9 | 39.3 | -328.69 | -82.33 | 14.76 | -6.98 | 20.3291066 | -81.15834288 | 18.9633086 | 40.09454734 | 0.00 | 0.00 | 0.00 | -328.7 | 14.8 | -313.9 | -12335.0 | 2960.7
139 | 195.469 | -310.5 | 29.9 | -326.57 | -90.37 | 16.09 | -2.79 | 22.3147093 | -80.63499826 | 7.582655674 | 43.69992143 | 0.00 | 0.00 | 0.00 | -326.6 | 16.1 | -310.5 | -9282.6 | 2618.5
140 | 196.875 | -308.0 | 19.9 | -324.26 | -98.36 | 16.25 | 1.60 | 24.28687044 | -80.06308212 | -4.347344491 | 44.13932935 | 0.00 | 0.00 | 0.00 | -324.3 | 16.3 | -308.0 | -6141.5 | 1993.2
141 | 198.281 | -306.5 | 10.3 | -321.74 | -106.29 | 15.24 | 5.88 | 26.24440208 | -79.44293898 | -15.96238882 | 41.38093695 | 0.00 | 0.00 | 0.00 | -321.7 | 15.2 | -306.5 | -3151.5 | 1153.3
142 | 199.688 | -305.9 | 1.8 | -319.04 | -114.15 | 13.12 | 9.73 | 28.18612508 | -78.77494238 | -26.42099209 | 35.62458388 | 0.00 | 0.00 | 0.00 | -319.0 | 13.1 | -305.9 | -540.0 | 218.7
143 | 201.094 | -306.1 | -4.9 | -316.14 | -121.95 | 10.05 | 12.87 | 30.11086981 | -78.05949471 | -34.96545082 | 27.28730564 | 0.00 | 0.00 | 0.00 | -316.1 | 10.0 | -306.1 | 1486.0 | -654.5
144 | 202.500 | -306.8 | -9.0 | -313.05 | -129.67 | 6.25 | 15.09 | 32.01747688 | -77.29702691 | -40.97673716 | 16.97312027 | 0.00 | 0.00 | 0.00 | -313.1 | 6.2 | -306.8 | 2748.7 | -1296.9
145 | 203.906 | -307.8 | -10.1 | -309.78 | -137.31 | 2.00 | 16.21 | 33.90479781 | -76.48799827 | -44.01934624 | 5.429268521 | 0.00 | 0.00 | 0.00 | -309.8 | 2.0 | -307.8 | 3113.0 | -1552.8
146 | 205.313 | -308.7 | -8.1 | -306.31 | -144.88 | -2.40 | 16.15 | 35.77169577 | -75.63289613 | -43.87284751 | -6.507922162 | 0.00 | 0.00 | 0.00 | -306.3 | -2.4 | -308.7 | 2500.9 | -1304.5
147 | 206.719 | -309.3 | -2.9 | -302.67 | -152.35 | -6.62 | 14.93 | 37.61704619 | -74.73223555 | -40.54785451 | -17.97362776 | 0.00 | 0.00 | 0.00 | -302.7 | -6.6 | -309.3 | 906.4 | -490.3
148 | 208.125 | -309.2 | 5.2 | -298.84 | -159.73 | -10.36 | 12.62 | 39.43973751 | -73.78655907 | -34.28525587 | -28.13718233 | 0.00 | 0.00 | 0.00 | -298.8 | -10.4 | -309.2 | -1593.7 | 888.4
149 | 209.531 | -308.2 | 15.7 | -294.83 | -167.02 | -13.35 | 9.40 | 41.23867181 | -72.79643633 | -25.53876353 | -36.26225803 | 0.00 | 0.00 | 0.00 | -294.8 | -13.4 | -308.2 | -4838.3 | 2769.8
150 | 210.938 | -306.0 | 28.1 | -290.64 | -174.20 | -15.38 | 5.50 | 43.01276547 | -71.76246374 | -14.94204221 | -41.76021042 | 0.00 | 0.00 | 0.00 | -290.6 | -15.4 | -306.0 | -8590.0 | 5044.4
151 | 212.344 | -302.6 | 41.5 | -286.28 | -181.28 | -16.29 | 1.20 | 44.76094985 | -70.68526412 | -3.262801784 | -44.23272459 | 0.00 | 0.00 | 0.00 | -286.3 | -16.3 | -302.6 | -12555.7 | 7572.7
152 | 213.750 | -297.8 | 55.1 | -281.74 | -188.25 | -16.02 | -3.19 | 46.48217191 | -69.56548634 | 8.652821678 | -43.50067214 | 0.00 | 0.00 | 0.00 | -281.7 | -16.0 | -297.8 | -16416.8 | 10203.7
153 | 215.156 | -291.6 | 68.1 | -277.04 | -195.11 | -14.59 | -7.34 | 48.17539484 | -68.40380491 | 19.94156665 | -39.61708873 | 0.00 | 0.00 | 0.00 | -277.0 | -14.6 | -291.6 | -19864.4 | 12790.2
154 | 216.563 | -284.3 | 79.6 | -272.16 | -201.85 | -12.10 | -10.97 | 49.83959872 | -67.20091959 | 29.78558763 | -32.86333168 | 0.00 | 0.00 | 0.00 | -272.2 | -12.1 | -284.3 | -22634.5 | 15199.2
155 | 217.969 | -275.9 | 88.9 | -267.13 | -208.47 | -8.74 | -13.80 | 51.47378109 | -65.95755495 | 37.47170628 | -23.72869631 | 0.00 | 0.00 | 0.00 | -267.1 | -8.7 | -275.9 | -24536.9 | 17315.2
156 | 219.375 | -266.7 | 95.5 | -261.93 | -214.96 | -4.74 | -15.63 | 53.07695758 | -64.67445994 | 42.44307968 | -12.87496746 | 0.00 | 0.00 | 0.00 | -261.9 | -4.7 | -266.7 | -25472.5 | 19040.5
157 | 220.781 | -257.0 | 99.0 | -256.58 | -221.33 | -0.40 | -16.33 | 54.6481625 | -63.35240746 | 44.33954243 | -1.088474672 | 0.00 | 0.00 | 0.00 | -256.6 | -0.4 | -257.0 | -25437.7 | 20292.5
158 | 222.188 | -247.1 | 99.2 | -251.07 | -227.56 | 3.97 | -15.84 | 56.1864494 | -61.99219385 | 43.02369984 | 10.77687579 | 0.00 | 0.00 | 0.00 | -251.1 | 4.0 | -247.1 | -24514.9 | 21004.2
159 | 223.594 | -237.4 | 96.3 | -245.41 | -233.65 | 8.05 | -14.21 | 57.69089169 | -60.59463847 | 38.59088191 | 21.86146457 | 0.00 | 0.00 | 0.00 | -245.4 | 8.0 | -237.4 | -22853.4 | 21128.0
160 | 225.000 | -228.1 | 90.5 | -239.60 | -239.60 | 11.55 | -11.55 | 59.16058314 | -59.16058314 | 31.36223684 | 31.36223684 | 0.00 | 0.00 | 0.00 | -239.6 | 11.5 | -228.1 | -20644.0 | 20644.0
161 | 226.406 | -219.4 | 82.5 | -233.65 | -245.41 | 14.21 | -8.05 | 60.59463847 | -57.69089169 | 21.86146457 | 38.59088191 | 0.00 | 0.00 | 0.00 | -233.6 | 14.2 | -219.4 | -18094.1 | 19571.7
162 | 227.813 | -211.7 | 72.8 | -227.56 | -251.07 | 15.84 | -3.97 | 61.99219385 | -56.1864494 | 10.77687579 | 43.02369984 | 0.00 | 0.00 | 0.00 | -227.6 | 15.8 | -211.7 | -15406.3 | 17981.3
163 | 229.219 | -205.0 | 62.3 | -221.33 | -256.58 | 16.33 | 0.40 | 63.35240746 | -54.6481625 | -1.088474672 | 44.33954243 | 0.00 | 0.00 | 0.00 | -221.3 | 16.3 | -205.0 | -12764.1 | 16000.5
164 | 230.625 | -199.3 | 51.8 | -214.96 | -261.93 | 15.63 | 4.74 | 64.67445994 | -53.07695758 | -12.87496746 | 42.44307968 | 0.00 | 0.00 | 0.00 | -215.0 | 15.6 | -199.3 | -10325.4 | 13813.5
165 | 232.031 | -194.7 | 42.2 | -208.47 | -267.13 | 13.80 | 8.74 | 65.95755495 | -51.47378109 | -23.72869631 | 37.47170628 | 0.00 | 0.00 | 0.00 | -208.5 | 13.8 | -194.7 | -8220.8 | 11649.4
166 | 233.438 | -190.9 | 34.3 | -201.85 | -272.16 | 10.97 | 12.10 | 67.20091959 | -49.83959872 | -32.86333168 | 29.78558763 | 0.00 | 0.00 | 0.00 | -201.9 | 11.0 | -190.9 | -6554.5 | 9760.9
167 | 234.844 | -187.8 | 28.8 | -195.11 | -277.04 | 7.34 | 14.59 | 68.40380491 | -48.17539484 | -39.61708873 | 19.94156665 | 0.00 | 0.00 | 0.00 | -195.1 | 7.3 | -187.8 | -5405.2 | 8394.8
168 | 236.250 | -185.1 | 26.1 | -188.25 | -281.74 | 3.19 | 16.02 | 69.56548634 | -46.48217191 | -43.50067214 | 8.652821678 | 0.00 | 0.00 | 0.00 | -188.3 | 3.2 | -185.1 | -4823.7 | 7761.0
169 | 237.656 | -182.5 | 26.5 | -181.28 | -286.28 | -1.20 | 16.29 | 70.68526412 | -44.76094985 | -44.23272459 | -3.262801784 | 0.00 | 0.00 | 0.00 | -181.3 | -1.2 | -182.5 | -4827.1 | 8003.5
170 | 239.063 | -179.7 | 30.0 | -174.20 | -290.64 | -5.50 | 15.38 | 71.76246374 | -43.01276547 | -41.76021042 | -14.94204221 | 0.00 | 0.00 | 0.00 | -174.2 | -5.5 | -179.7 | -5391.5 | 9181.1
171 | 240.469 | -176.4 | 36.5 | -167.02 | -294.83 | -9.40 | 13.35 | 72.79643633 | -41.23867181 | -36.26225803 | -25.53876353 | 0.00 | 0.00 | 0.00 | -167.0 | -9.4 | -176.4 | -6445.3 | 11259.0
172 | 241.875 | -172.4 | 45.6 | -159.73 | -298.84 | -12.62 | 10.36 | 73.78655907 | -39.43973751 | -28.13718233 | -34.28525587 | 0.00 | 0.00 | 0.00 | -159.7 | -12.6 | -172.4 | -7867.9 | 14114.6
173 | 243.281 | -167.3 | 56.8 | -152.35 | -302.67 | -14.93 | 6.62 | 74.73223555 | -37.61704619 | -17.97362776 | -40.54785451 | 0.00 | 0.00 | 0.00 | -152.3 | -14.9 | -167.3 | -9494.5 | 17554.5
174 | 244.688 | -161.0 | 69.1 | -144.88 | -306.31 | -16.15 | 2.40 | 75.63289613 | -35.77169577 | -6.507922162 | -43.87284751 | 0.00 | 0.00 | 0.00 | -144.9 | -16.2 | -161.0 | -11131.1 | 21339.5
175 | 246.094 | -153.5 | 81.9 | -137.31 | -309.78 | -16.21 | -2.00 | 76.48799827 | -33.90479781 | 5.429268521 | -44.01934624 | 0.00 | 0.00 | 0.00 | -137.3 | -16.2 | -153.5 | -12576.1 | 25212.3
176 | 247.500 | -144.8 | 94.3 | -129.67 | -313.05 | -15.09 | -6.25 | 77.29702691 | -32.01747688 | 16.97312027 | -40.97673716 | 0.00 | 0.00 | 0.00 | -129.7 | -15.1 | -144.8 | -13646.3 | 28922.4
177 | 248.906 | -134.8 | 105.3 | -121.95 | -316.14 | -12.87 | -10.05 | 78.05949471 | -30.11086981 | 27.28730564 | -34.96545082 | 0.00 | 0.00 | 0.00 | -121.9 | -12.9 | -134.8 | -14203.1 | 32246.1
178 | 250.313 | -123.9 | 114.4 | -114.15 | -319.04 | -9.73 | -13.12 | 78.77494238 | -28.18612508 | 35.62458388 | -26.42099209 | 0.00 | 0.00 | 0.00 | -114.2 | -9.7 | -123.9 | -14172.0 | 34997.4
179 | 251.719 | -112.2 | 120.8 | -106.29 | -321.74 | -5.88 | -15.24 | 79.44293898 | -26.24440208 | 41.38093695 | -15.96238882 | 0.00 | 0.00 | 0.00 | -106.3 | -5.9 | -112.2 | -13552.4 | 37033.5
180 | 253.125 | -100.0 | 124.2 | -98.36 | -324.26 | -1.60 | -16.25 | 80.06308212 | -24.28687044 | 44.13932935 | -4.347344491 | 0.00 | 0.00 | 0.00 | -98.4 | -1.6 | -100.0 | -12415.6 | 38254.9
181 | 254.531 | -87.6 | 124.3 | -90.37 | -326.57 | 2.79 | -16.09 | 80.63499826 | -22.3147093 | 43.69992143 | 7.582655674 | 0.00 | 0.00 | 0.00 | -90.4 | 2.8 | -87.6 | -10889.6 | 38603.8
182 | 255.938 | -75.4 | 121.3 | -82.33 | -328.69 | 6.98 | -14.76 | 81.15834288 | -20.3291066 | 40.09454734 | 18.9633086 | 0.00 | 0.00 | 0.00 | -82.3 | 7.0 | -75.4 | -9136.5 | 38064.8
183 | 257.344 | -63.6 | 115.2 | -74.24 | -330.61 | 10.67 | -12.37 | 81.63280076 | -18.33125842 | 33.58440877 | 28.97011024 | 0.00 | 0.00 | 0.00 | -74.2 | 10.7 | -63.6 | -7325.0 | 36667.6
184 | 258.750 | -52.5 | 106.7 | -66.11 | -332.34 | 13.58 | -9.07 | 82.05808609 | -16.32236817 | 24.64115137 | 36.87808914 | 0.00 | 0.00 | 0.00 | -66.1 | 13.6 | -52.5 | -5604.7 | 34491.9
185 | 260.156 | -42.4 | 96.3 | -57.93 | -333.86 | 15.51 | -5.12 | 82.43394269 | -14.30364593 | 13.91269508 | 42.1143291 | 0.00 | 0.00 | 0.00 | -57.9 | 15.5 | -42.4 | -4087.4 | 31672.5
186 | 261.563 | -33.4 | 84.9 | -49.72 | -335.18 | 16.31 | -0.80 | 82.76014417 | -12.27630771 | 2.176293687 | 44.29947568 | 0.00 | 0.00 | 0.00 | -49.7 | 16.3 | -33.4 | -2837.6 | 28400.8
187 | 262.969 | -25.5 | 73.3 | -41.48 | -336.30 | 15.93 | 3.58 | 83.03649404 | -10.24157471 | -9.717775546 | 43.27521968 | 0.00 | 0.00 | 0.00 | -41.5 | 15.9 | -25.5 | -1872.9 | 24919.3
188 | 264.375 | -18.8 | 62.4 | -33.21 | -337.21 | 14.40 | 7.70 | 83.26282582 | -8.200672563 | -20.90781266 | 39.11576626 | 0.00 | 0.00 | 0.00 | -33.2 | 14.4 | -18.8 | -1173.0 | 21507.0
189 | 265.781 | -13.1 | 52.9 | -24.93 | -337.93 | 11.83 | 11.26 | 83.4390032 | -6.154830638 | -30.5831233 | 32.12245895 | 0.00 | 0.00 | 0.00 | -24.9 | 11.8 | -13.1 | -692.4 | 18456.6
190 | 267.188 | -8.2 | 45.5 | -16.63 | -338.44 | 8.40 | 14.01 | 83.56492003 | -4.105281273 | -38.04275186 | 22.80194796 | 0.00 | 0.00 | 0.00 | -16.6 | 8.4 | -8.2 | -374.7 | 16044.0
191 | 268.594 | -4.0 | 40.9 | -8.32 | -338.74 | 4.36 | 15.74 | 83.64050049 | -2.05325904 | -42.74626414 | 11.82948445 | 0.00 | 0.00 | 0.00 | -8.3 | 4.4 | -4.0 | -162.0 | 14496.3
192 | 270.000 | 0.0 | 39.3 | 0.00 | -338.85 | 0.00 | 16.33 | 83.66569903 | 0 | -44.35290069 | 0 | 0.00 | 0.00 | 0.00 | 0.0 | 0.0 | 0.0 | 0.0 | 13963.0
193 | 271.406 | 4.0 | 40.9 | 8.32 | -338.74 | -4.36 | 15.74 | 83.64050049 | 2.05325904 | -42.74626414 | -11.82948445 | 0.00 | 0.00 | 0.00 | 8.3 | -4.4 | 4.0 | 162.0 | 14496.3
194 | 272.813 | 8.2 | 45.5 | 16.63 | -338.44 | -8.40 | 14.01 | 83.56492003 | 4.105281273 | -38.04275186 | -22.80194796 | 0.00 | 0.00 | 0.00 | 16.6 | -8.4 | 8.2 | 374.7 | 16044.0
195 | 274.219 | 13.1 | 52.9 | 24.93 | -337.93 | -11.83 | 11.26 | 83.4390032 | 6.154830638 | -30.5831233 | -32.12245895 | 0.00 | 0.00 | 0.00 | 24.9 | -11.8 | 13.1 | 692.4 | 18456.6
196 | 275.625 | 18.8 | 62.4 | 33.21 | -337.21 | -14.40 | 7.70 | 83.26282582 | 8.200672563 | -20.90781266 | -39.11576626 | 0.00 | 0.00 | 0.00 | 33.2 | -14.4 | 18.8 | 1173.0 | 21507.0
197 | 277.031 | 25.5 | 73.3 | 41.48 | -336.30 | -15.93 | 3.58 | 83.03649404 | 10.24157471 | -9.717775546 | -43.27521968 | 0.00 | 0.00 | 0.00 | 41.5 | -15.9 | 25.5 | 1872.9 | 24919.3
198 | 278.438 | 33.4 | 84.9 | 49.72 | -335.18 | -16.31 | -0.80 | 82.76014417 | 12.27630771 | 2.176293687 | -44.29947568 | 0.00 | 0.00 | 0.00 | 49.7 | -16.3 | 33.4 | 2837.6 | 28400.8
199 | 279.844 | 42.4 | 96.3 | 57.93 | -333.86 | -15.51 | -5.12 | 82.43394269 | 14.30364593 | 13.91269508 | -42.1143291 | 0.00 | 0.00 | 0.00 | 57.9 | -15.5 | 42.4 | 4087.4 | 31672.5
200 | 281.250 | 52.5 | 106.7 | 66.11 | -332.34 | -13.58 | -9.07 | 82.05808609 | 16.32236817 | 24.64115137 | -36.87808914 | 0.00 | 0.00 | 0.00 | 66.1 | -13.6 | 52.5 | 5604.7 | 34491.9
201 | 282.656 | 63.6 | 115.2 | 74.24 | -330.61 | -10.67 | -12.37 | 81.63280076 | 18.33125842 | 33.58440877 | -28.97011024 | 0.00 | 0.00 | 0.00 | 74.2 | -10.7 | 63.6 | 7325.0 | 36667.6
202 | 284.063 | 75.4 | 121.3 | 82.33 | -328.69 | -6.98 | -14.76 | 81.15834288 | 20.3291066 | 40.09454734 | -18.9633086 | 0.00 | 0.00 | 0.00 | 82.3 | -7.0 | 75.4 | 9136.5 | 38064.8
203 | 285.469 | 87.6 | 124.3 | 90.37 | -326.57 | -2.79 | -16.09 | 80.63499826 | 22.3147093 | 43.69992143 | -7.582655674 | 0.00 | 0.00 | 0.00 | 90.4 | -2.8 | 87.6 | 10889.6 | 38603.8
204 | 286.875 | 100.0 | 124.2 | 98.36 | -324.26 | 1.60 | -16.25 | 80.06308212 | 24.28687044 | 44.13932935 | 4.347344491 | 0.00 | 0.00 | 0.00 | 98.4 | 1.6 | 100.0 | 12415.6 | 38254.9
205 | 288.281 | 112.2 | 120.8 | 106.29 | -321.74 | 5.88 | -15.24 | 79.44293898 | 26.24440208 | 41.38093695 | 15.96238882 | 0.00 | 0.00 | 0.00 | 106.3 | 5.9 | 112.2 | 13552.4 | 37033.5
206 | 289.688 | 123.9 | 114.4 | 114.15 | -319.04 | 9.73 | -13.12 | 78.77494238 | 28.18612508 | 35.62458388 | 26.42099209 | 0.00 | 0.00 | 0.00 | 114.2 | 9.7 | 123.9 | 14172.0 | 34997.4
207 | 291.094 | 134.8 | 105.3 | 121.95 | -316.14 | 12.87 | -10.05 | 78.05949471 | 30.11086981 | 27.28730564 | 34.96545082 | 0.00 | 0.00 | 0.00 | 121.9 | 12.9 | 134.8 | 14203.1 | 32246.1
208 | 292.500 | 144.8 | 94.3 | 129.67 | -313.05 | 15.09 | -6.25 | 77.29702691 | 32.01747688 | 16.97312027 | 40.97673716 | 0.00 | 0.00 | 0.00 | 129.7 | 15.1 | 144.8 | 13646.3 | 28922.4
209 | 293.906 | 153.5 | 81.9 | 137.31 | -309.78 | 16.21 | -2.00 | 76.48799827 | 33.90479781 | 5.429268521 | 44.01934624 | 0.00 | 0.00 | 0.00 | 137.3 | 16.2 | 153.5 | 12576.1 | 25212.3
210 | 295.313 | 161.0 | 69.1 | 144.88 | -306.31 | 16.15 | 2.40 | 75.63289613 | 35.77169577 | -6.507922162 | 43.87284751 | 0.00 | 0.00 | 0.00 | 144.9 | 16.2 | 161.0 | 11131.1 | 21339.5
211 | 296.719 | 167.3 | 56.8 | 152.35 | -302.67 | 14.93 | 6.62 | 74.73223555 | 37.61704619 | -17.97362776 | 40.54785451 | 0.00 | 0.00 | 0.00 | 152.3 | 14.9 | 167.3 | 9494.5 | 17554.5
212 | 298.125 | 172.4 | 45.6 | 159.73 | -298.84 | 12.62 | 10.36 | 73.78655907 | 39.43973751 | -28.13718233 | 34.28525587 | 0.00 | 0.00 | 0.00 | 159.7 | 12.6 | 172.4 | 7867.9 | 14114.6
213 | 299.531 | 176.4 | 36.5 | 167.02 | -294.83 | 9.40 | 13.35 | 72.79643633 | 41.23867181 | -36.26225803 | 25.53876353 | 0.00 | 0.00 | 0.00 | 167.0 | 9.4 | 176.4 | 6445.3 | 11259.0
214 | 300.938 | 179.7 | 30.0 | 174.20 | -290.64 | 5.50 | 15.38 | 71.76246374 | 43.01276547 | -41.76021042 | 14.94204221 | 0.00 | 0.00 | 0.00 | 174.2 | 5.5 | 179.7 | 5391.5 | 9181.1
215 | 302.344 | 182.5 | 26.5 | 181.28 | -286.28 | 1.20 | 16.29 | 70.68526412 | 44.76094985 | -44.23272459 | 3.262801784 | 0.00 | 0.00 | 0.00 | 181.3 | 1.2 | 182.5 | 4827.1 | 8003.5
216 | 303.750 | 185.1 | 26.1 | 188.25 | -281.74 | -3.19 | 16.02 | 69.56548634 | 46.48217191 | -43.50067214 | -8.652821678 | 0.00 | 0.00 | 0.00 | 188.3 | -3.2 | 185.1 | 4823.7 | 7761.0
217 | 305.156 | 187.8 | 28.8 | 195.11 | -277.04 | -7.34 | 14.59 | 68.40380491 | 48.17539484 | -39.61708873 | -19.94156665 | 0.00 | 0.00 | 0.00 | 195.1 | -7.3 | 187.8 | 5405.2 | 8394.8
218 | 306.563 | 190.9 | 34.3 | 201.85 | -272.16 | -10.97 | 12.10 | 67.20091959 | 49.83959872 | -32.86333168 | -29.78558763 | 0.00 | 0.00 | 0.00 | 201.9 | -11.0 | 190.9 | 6554.5 | 9760.9
219 | 307.969 | 194.7 | 42.2 | 208.47 | -267.13 | -13.80 | 8.74 | 65.95755495 | 51.47378109 | -23.72869631 | -37.47170628 | 0.00 | 0.00 | 0.00 | 208.5 | -13.8 | 194.7 | 8220.8 | 11649.4
220 | 309.375 | 199.3 | 51.8 | 214.96 | -261.93 | -15.63 | 4.74 | 64.67445994 | 53.07695758 | -12.87496746 | -42.44307968 | 0.00 | 0.00 | 0.00 | 215.0 | -15.6 | 199.3 | 10325.4 | 13813.5
221 | 310.781 | 205.0 | 62.3 | 221.33 | -256.58 | -16.33 | 0.40 | 63.35240746 | 54.6481625 | -1.088474672 | -44.33954243 | 0.00 | 0.00 | 0.00 | 221.3 | -16.3 | 205.0 | 12764.1 | 16000.5
222 | 312.188 | 211.7 | 72.8 | 227.56 | -251.07 | -15.84 | -3.97 | 61.99219385 | 56.1864494 | 10.77687579 | -43.02369984 | 0.00 | 0.00 | 0.00 | 227.6 | -15.8 | 211.7 | 15406.3 | 17981.3
223 | 313.594 | 219.4 | 82.5 | 233.65 | -245.41 | -14.21 | -8.05 | 60.59463847 | 57.69089169 | 21.86146457 | -38.59088191 | 0.00 | 0.00 | 0.00 | 233.6 | -14.2 | 219.4 | 18094.1 | 19571.7
224 | 315.000 | 228.1 | 90.5 | 239.60 | -239.60 | -11.55 | -11.55 | 59.16058314 | 59.16058314 | 31.36223684 | -31.36223684 | 0.00 | 0.00 | 0.00 | 239.6 | -11.5 | 228.1 | 20644.0 | 20644.0
225 | 316.406 | 237.4 | 96.3 | 245.41 | -233.65 | -8.05 | -14.21 | 57.69089169 | 60.59463847 | 38.59088191 | -21.86146457 | 0.00 | 0.00 | 0.00 | 245.4 | -8.0 | 237.4 | 22853.4 | 21128.0
226 | 317.813 | 247.1 | 99.2 | 251.07 | -227.56 | -3.97 | -15.84 | 56.1864494 | 61.99219385 | 43.02369984 | -10.77687579 | 0.00 | 0.00 | 0.00 | 251.1 | -4.0 | 247.1 | 24514.9 | 21004.2
227 | 319.219 | 257.0 | 99.0 | 256.58 | -221.33 | 0.40 | -16.33 | 54.6481625 | 63.35240746 | 44.33954243 | 1.088474672 | 0.00 | 0.00 | 0.00 | 256.6 | 0.4 | 257.0 | 25437.7 | 20292.5
228 | 320.625 | 266.7 | 95.5 | 261.93 | -214.96 | 4.74 | -15.63 | 53.07695758 | 64.67445994 | 42.44307968 | 12.87496746 | 0.00 | 0.00 | 0.00 | 261.9 | 4.7 | 266.7 | 25472.5 | 19040.5
229 | 322.031 | 275.9 | 88.9 | 267.13 | -208.47 | 8.74 | -13.80 | 51.47378109 | 65.95755495 | 37.47170628 | 23.72869631 | 0.00 | 0.00 | 0.00 | 267.1 | 8.7 | 275.9 | 24536.9 | 17315.2
230 | 323.438 | 284.3 | 79.6 | 272.16 | -201.85 | 12.10 | -10.97 | 49.83959872 | 67.20091959 | 29.78558763 | 32.86333168 | 0.00 | 0.00 | 0.00 | 272.2 | 12.1 | 284.3 | 22634.5 | 15199.2
231 | 324.844 | 291.6 | 68.1 | 277.04 | -195.11 | 14.59 | -7.34 | 48.17539484 | 68.40380491 | 19.94156665 | 39.61708873 | 0.00 | 0.00 | 0.00 | 277.0 | 14.6 | 291.6 | 19864.4 | 12790.2
232 | 326.250 | 297.8 | 55.1 | 281.74 | -188.25 | 16.02 | -3.19 | 46.48217191 | 69.56548634 | 8.652821678 | 43.50067214 | 0.00 | 0.00 | 0.00 | 281.7 | 16.0 | 297.8 | 16416.8 | 10203.7
233 | 327.656 | 302.6 | 41.5 | 286.28 | -181.28 | 16.29 | 1.20 | 44.76094985 | 70.68526412 | -3.262801784 | 44.23272459 | 0.00 | 0.00 | 0.00 | 286.3 | 16.3 | 302.6 | 12555.7 | 7572.7
234 | 329.063 | 306.0 | 28.1 | 290.64 | -174.20 | 15.38 | 5.50 | 43.01276547 | 71.76246374 | -14.94204221 | 41.76021042 | 0.00 | 0.00 | 0.00 | 290.6 | 15.4 | 306.0 | 8590.0 | 5044.4
235 | 330.469 | 308.2 | 15.7 | 294.83 | -167.02 | 13.35 | 9.40 | 41.23867181 | 72.79643633 | -25.53876353 | 36.26225803 | 0.00 | 0.00 | 0.00 | 294.8 | 13.4 | 308.2 | 4838.3 | 2769.8
236 | 331.875 | 309.2 | 5.2 | 298.84 | -159.73 | 10.36 | 12.62 | 39.43973751 | 73.78655907 | -34.28525587 | 28.13718233 | 0.00 | 0.00 | 0.00 | 298.8 | 10.4 | 309.2 | 1593.7 | 888.4
237 | 333.281 | 309.3 | -2.9 | 302.67 | -152.35 | 6.62 | 14.93 | 37.61704619 | 74.73223555 | -40.54785451 | 17.97362776 | 0.00 | 0.00 | 0.00 | 302.7 | 6.6 | 309.3 | -906.4 | -490.3
238 | 334.688 | 308.7 | -8.1 | 306.31 | -144.88 | 2.40 | 16.15 | 35.77169577 | 75.63289613 | -43.87284751 | 6.507922162 | 0.00 | 0.00 | 0.00 | 306.3 | 2.4 | 308.7 | -2500.9 | -1304.5
239 | 336.094 | 307.8 | -10.1 | 309.78 | -137.31 | -2.00 | 16.21 | 33.90479781 | 76.48799827 | -44.01934624 | -5.429268521 | 0.00 | 0.00 | 0.00 | 309.8 | -2.0 | 307.8 | -3113.0 | -1552.8
240 | 337.500 | 306.8 | -9.0 | 313.05 | -129.67 | -6.25 | 15.09 | 32.01747688 | 77.29702691 | -40.97673716 | -16.97312027 | 0.00 | 0.00 | 0.00 | 313.1 | -6.2 | 306.8 | -2748.7 | -1296.9
241 | 338.906 | 306.1 | -4.9 | 316.14 | -121.95 | -10.05 | 12.87 | 30.11086981 | 78.05949471 | -34.96545082 | -27.28730564 | 0.00 | 0.00 | 0.00 | 316.1 | -10.0 | 306.1 | -1486.0 | -654.5
242 | 340.313 | 305.9 | 1.8 | 319.04 | -114.15 | -13.12 | 9.73 | 28.18612508 | 78.77494238 | -26.42099209 | -35.62458388 | 0.00 | 0.00 | 0.00 | 319.0 | -13.1 | 305.9 | 540.0 | 218.7
243 | 341.719 | 306.5 | 10.3 | 321.74 | -106.29 | -15.24 | 5.88 | 26.24440208 | 79.44293898 | -15.96238882 | -41.38093695 | 0.00 | 0.00 | 0.00 | 321.7 | -15.2 | 306.5 | 3151.5 | 1153.3
244 | 343.125 | 308.0 | 19.9 | 324.26 | -98.36 | -16.25 | 1.60 | 24.28687044 | 80.06308212 | -4.347344491 | -44.13932935 | 0.00 | 0.00 | 0.00 | 324.3 | -16.3 | 308.0 | 6141.5 | 1993.2
245 | 344.531 | 310.5 | 29.9 | 326.57 | -90.37 | -16.09 | -2.79 | 22.3147093 | 80.63499826 | 7.582655674 | -43.69992143 | 0.00 | 0.00 | 0.00 | 326.6 | -16.1 | 310.5 | 9282.6 | 2618.5
246 | 345.938 | 313.9 | 39.3 | 328.69 | -82.33 | -14.76 | -6.98 | 20.3291066 | 81.15834288 | 18.9633086 | -40.09454734 | 0.00 | 0.00 | 0.00 | 328.7 | -14.8 | 313.9 | 12335.0 | 2960.7
247 | 347.344 | 318.2 | 47.3 | 330.61 | -74.24 | -12.37 | -10.67 | 18.33125842 | 81.63280076 | 28.97011024 | -33.58440877 | 0.00 | 0.00 | 0.00 | 330.6 | -12.4 | 318.2 | 15053.6 | 3007.2
248 | 348.750 | 323.3 | 53.2 | 332.34 | -66.11 | -9.07 | -13.58 | 16.32236817 | 82.05808609 | 36.87808914 | -24.64115137 | 0.00 | 0.00 | 0.00 | 332.3 | -9.1 | 323.3 | 17197.7 | 2794.5
249 | 350.156 | 328.7 | 56.4 | 333.86 | -57.93 | -5.12 | -15.51 | 14.30364593 | 82.43394269 | 42.1143291 | -13.91269508 | 0.00 | 0.00 | 0.00 | 333.9 | -5.1 | 328.7 | 18546.6 | 2393.5
250 | 351.563 | 334.4 | 56.6 | 335.18 | -49.72 | -0.80 | -16.31 | 12.27630771 | 82.76014417 | 44.29947568 | -2.176293687 | 0.00 | 0.00 | 0.00 | 335.2 | -0.8 | 334.4 | 18917.7 | 1890.1
251 | 352.969 | 339.9 | 53.5 | 336.30 | -41.48 | 3.58 | -15.93 | 10.24157471 | 83.03649404 | 43.27521968 | 9.717775546 | 0.00 | 0.00 | 0.00 | 336.3 | 3.6 | 339.9 | 18189.1 | 1367.1
252 | 354.375 | 344.9 | 47.3 | 337.21 | -33.21 | 7.70 | -14.40 | 8.200672563 | 83.26282582 | 39.11576626 | 20.90781266 | 0.00 | 0.00 | 0.00 | 337.2 | 7.7 | 344.9 | 16320.0 | 890.1
253 | 355.781 | 349.2 | 38.3 | 337.93 | -24.93 | 11.26 | -11.83 | 6.154830638 | 83.4390032 | 32.12245895 | 30.5831233 | 0.00 | 0.00 | 0.00 | 337.9 | 11.3 | 349.2 | 13366.0 | 501.4
254 | 357.188 | 352.4 | 26.9 | 338.44 | -16.63 | 14.01 | -8.40 | 4.105281273 | 83.56492003 | 22.80194796 | 38.04275186 | 0.00 | 0.00 | 0.00 | 338.4 | 14.0 | 352.4 | 9483.3 | 221.5
255 | 358.594 | 354.5 | 13.9 | 338.74 | -8.32 | 15.74 | -4.36 | 2.05325904 | 83.64050049 | 11.82948445 | 42.74626414 | 0.00 | 0.00 | 0.00 | 338.7 | 15.7 | 354.5 | 4921.2 | 55.0
|  | Sqr V | Sqr I | Sqr V1 |  | Sqr Vn |  | Sqr I1 |  | Sqr In |  | Sqr V1L | Sqr VnL | Sqr VL | Sqr V1c | Sqr Vnc | Sqr Vc
0 |  | 126150 | 0 | 114816.6667 |  | 266.6666667 |  | 0 |  | 0 |  | 0 | 0 | 0 | 114816.6667 | 266.6666667 | 126150
1 |  | 125657.7891 | 192.7305667 | 114747.5158 |  | 247.697148 |  | 4.215872683 |  | 139.9367023 |  | 0 | 0 | 0 | 114747.5158 | 247.697148 | 125657.7891
2 |  | 124217.1789 | 723.9989849 | 114540.2299 |  | 196.1862316 |  | 16.85333433 |  | 519.9288307 |  | 0 | 0 | 0 | 114540.2299 | 196.1862316 | 124217.1789
3 |  | 121932.3382 | 1465.150898 | 114195.3081 |  | 126.7909768 |  | 37.88194018 |  | 1031.852369 |  | 0 | 0 | 0 | 114195.3081 | 126.7909768 | 121932.3382
4 |  | 118964.5092 | 2238.845383 | 113713.5816 |  | 59.25730226 |  | 67.25103048 |  | 1530.04317 |  | 0 | 0 | 0 | 113713.5816 | 59.25730226 | 118964.5092
5 |  | 115515.4977 | 2864.047282 | 113096.2109 |  | 12.80142758 |  | 104.8898525 |  | 1872.744638 |  | 0 | 0 | 0 | 113096.2109 | 12.80142758 | 115515.4977
6 |  | 111808.1869 | 3200.819267 | 112344.6831 |  | 0.6420364437 |  | 150.7077311 |  | 1962.443546 |  | 0 | 0 | 0 | 112344.6831 | 0.6420364437 | 111808.1869
7 |  | 108066.744 | 3182.987906 | 111460.8089 |  | 26.2389958 |  | 204.5942869 |  | 1773.616715 |  | 0 | 0 | 0 | 111460.8089 | 26.2389958 | 108066.744
8 |  | 104498.8539 | 2830.288658 | 110446.7175 |  | 82.30887568 |  | 266.4197026 |  | 1359.993459 |  | 0 | 0 | 0 | 110446.7175 | 82.30887568 | 104498.8539
9 |  | 101281.5823 | 2237.419477 | 109304.852 |  | 152.8973966 |  | 336.0350351 |  | 839.2672872 |  | 0 | 0 | 0 | 109304.852 | 152.8973966 | 101281.5823
10 |  | 98551.54596 | 1543.893892 | 108037.9633 |  | 217.9191046 |  | 413.2725753 |  | 359.607073 |  | 0 | 0 | 0 | 108037.9633 | 217.9191046 | 98551.54596
11 |  | 96399.21292 | 893.8524321 | 106649.1033 |  | 258.872542 |  | 497.9462509 |  | 57.49666708 |  | 0 | 0 | 0 | 106649.1033 | 258.872542 | 96399.21292
12 |  | 94866.5774 | 397.5846951 | 105141.618 |  | 264.1047041 |  | 589.8520758 |  | 18.89940413 |  | 0 | 0 | 0 | 105141.618 | 264.1047041 | 94866.5774
13 |  | 93947.27315 | 105.7197969 | 103519.139 |  | 232.1268167 |  | 688.7686408 |  | 254.7978567 |  | 0 | 0 | 0 | 103519.139 | 232.1268167 | 93947.27315
14 |  | 93588.38792 | 3.11569446 | 101785.5751 |  | 172.037957 |  | 794.4576471 |  | 698.0688233 |  | 0 | 0 | 0 | 101785.5751 | 172.037957 | 93588.38792
15 |  | 93693.69831 | 23.56695674 | 99945.10252 |  | 100.935976 |  | 906.6644807 |  | 1222.582751 |  | 0 | 0 | 0 | 99945.10252 | 100.935976 | 93693.69831
16 |  | 94128.55004 | 80.26834476 | 98002.15513 |  | 39.05242918 |  | 1025.118826 |  | 1679.092988 |  | 0 | 0 | 0 | 98002.15513 | 39.05242918 | 94128.55004
17 |  | 94726.94953 | 102.3040898 | 95961.41367 |  | 3.995832907 |  | 1149.535315 |  | 1937.702843 |  | 0 | 0 | 0 | 95961.41367 | 3.995832907 | 94726.94953
18 |  | 95301.44915 | 65.62865962 | 93827.79446 |  | 5.741288569 |  | 1279.614218 |  | 1924.826749 |  | 0 | 0 | 0 | 93827.79446 | 5.741288569 | 95301.44915
19 |  | 95656.04642 | 8.589637396 | 91606.43757 |  | 43.79213935 |  | 1415.042164 |  | 1644.128505 |  | 0 | 0 | 0 | 91606.43757 | 43.79213935 | 95656.04642
20 |  | 95601.64895 | 26.56868094 | 89302.69446 |  | 107.3212904 |  | 1555.492895 |  | 1175.47877 |  | 0 | 0 | 0 | 89302.69446 | 107.3212904 | 95601.64895
21 |  | 94972.86069 | 246.4871198 | 86922.11504 |  | 178.2519805 |  | 1700.628052 |  | 652.2284427 |  | 0 | 0 | 0 | 86922.11504 | 178.2519805 | 94972.86069
22 |  | 93644.15712 | 787.9655041 | 84470.43433 |  | 236.4013938 |  | 1850.097993 |  | 223.2646255 |  | 0 | 0 | 0 | 84470.43433 | 236.4013938 | 93644.15712
23 |  | 91543.16153 | 1722.096293 | 81953.55866 |  | 265.2235347 |  | 2003.542631 |  | 10.64587548 |  | 0 | 0 | 0 | 81953.55866 | 265.2235347 | 91543.16153
24 |  | 88658.85959 | 3039.867518 | 79377.55138 |  | 256.517271 |  | 2160.592305 |  | 74.871323 |  | 0 | 0 | 0 | 79377.55138 | 256.517271 | 88658.85959
25 |  | 85043.21687 | 4639.920444 | 76748.61833 |  | 212.7599073 |  | 2320.868668 |  | 397.6660806 |  | 0 | 0 | 0 | 76748.61833 | 212.7599073 | 85043.21687
26 |  | 80805.68373 | 6340.170302 | 74073.09285 |  | 146.4022854 |  | 2483.985601 |  | 887.1812307 |  | 0 | 0 | 0 | 74073.09285 | 146.4022854 | 80805.68373
27 |  | 76101.26213 | 7911.299724 | 71357.42049 |  | 76.32598754 |  | 2649.55014 |  | 1404.128771 |  | 0 | 0 | 0 | 71357.42049 | 76.32598754 | 76101.26213
28 |  | 71113.89782 | 9124.077518 | 68608.14357 |  | 22.47071836 |  | 2817.163426 |  | 1801.415013 |  | 0 | 0 | 0 | 68608.14357 | 22.47071836 | 71113.89782
29 |  | 66037.69597 | 9798.565726 | 65831.88532 |  | 0.1606058393 |  | 2986.421664 |  | 1965.995023 |  | 0 | 0 | 0 | 65831.88532 | 0.1606058393 | 66037.69597
30 |  | 61058.67458 | 9842.653712 | 63035.334 |  | 15.74383142 |  | 3156.917096 |  | 1851.038748 |  | 0 | 0 | 0 | 63035.334 | 15.74383142 | 61058.67458
31 |  | 56339.43351 | 9270.179927 | 60225.22674 |  | 64.78630077 |  | 3328.238984 |  | 1489.256167 |  | 0 | 0 | 0 | 60225.22674 | 64.78630077 | 56339.43351
32 |  | 52008.33333 | 8194.380938 | 57408.33333 |  | 133.3333333 |  | 3499.974597 |  | 983.5898999 |  | 0 | 0 | 0 | 57408.33333 | 133.3333333 | 52008.33333
33 |  | 48153.76011 | 6799.008928 | 54591.43993 |  | 201.8803659 |  | 3671.710211 |  | 477.9236332 |  | 0 | 0 | 0 | 54591.43993 | 201.8803659 | 48153.76011
34 |  | 44823.06171 | 5295.337497 | 51781.33267 |  | 250.9228352 |  | 3843.032099 |  | 116.1410518 |  | 0 | 0 | 0 | 51781.33267 | 250.9228352 | 44823.06171
35 |  | 42025.01835 | 3876.797326 | 48984.78135 |  | 266.5060608 |  | 4013.527531 |  | 1.184777111 |  | 0 | 0 | 0 | 48984.78135 | 266.5060608 | 42025.01835
36 |  | 39734.40553 | 2683.187421 | 46208.5231 |  | 244.1959483 |  | 4182.785769 |  | 165.7647872 |  | 0 | 0 | 0 | 46208.5231 | 244.1959483 | 39734.40553
37 |  | 37897.34818 | 1783.276502 | 43459.24617 |  | 190.3406791 |  | 4350.399055 |  | 563.0510284 |  | 0 | 0 | 0 | 43459.24617 | 190.3406791 | 37897.34818
38 |  | 36436.64916 | 1179.069943 | 40743.57382 |  | 120.2643813 |  | 4515.963594 |  | 1079.998569 |  | 0 | 0 | 0 | 40743.57382 | 120.2643813 | 36436.64916
39 |  | 35256.90701 | 828.6750287 | 38068.04833 |  | 53.9067594 |  | 4679.080526 |  | 1569.513719 |  | 0 | 0 | 0 | 38068.04833 | 53.9067594 | 35256.90701
40 |  | 34249.78879 | 679.3745391 | 35439.11529 |  | 10.14939567 |  | 4839.356889 |  | 1892.308477 |  | 0 | 0 | 0 | 35439.11529 | 10.14939567 | 34249.78879
41 |  | 33300.10047 | 699.7368476 | 32863.10801 |  | 1.443132005 |  | 4996.406563 |  | 1956.533924 |  | 0 | 0 | 0 | 32863.10801 | 1.443132005 | 33300.10047
42 |  | 32293.19999 | 900.135204 | 30346.23233 |  | 30.26527288 |  | 5149.851202 |  | 1743.915174 |  | 0 | 0 | 0 | 30346.23233 | 30.26527288 | 32293.19999
43 |  | 31123.85028 | 1334.746184 | 27894.55163 |  | 88.41468621 |  | 5299.321142 |  | 1314.951357 |  | 0 | 0 | 0 | 27894.55163 | 88.41468621 | 31123.85028
44 |  | 29705.95121 | 2083.865597 | 25513.97221 |  | 159.3453763 |  | 5444.4563 |  | 791.7010296 |  | 0 | 0 | 0 | 25513.97221 | 159.3453763 | 29705.95121
45 |  | 27981.93593 | 3221.539559 | 23210.22909 |  | 222.8745273 |  | 5584.907031 |  | 323.0512947 |  | 0 | 0 | 0 | 23210.22909 | 222.8745273 | 27981.93593
46 |  | 25930.19476 | 4778.262026 | 20988.87221 |  | 260.9253781 |  | 5720.334977 |  | 42.35305087 |  | 0 | 0 | 0 | 20988.87221 | 260.9253781 | 25930.19476
47 |  | 23568.86757 | 6710.438599 | 18855.253 |  | 262.6708338 |  | 5850.41388 |  | 29.47695667 |  | 0 | 0 | 0 | 18855.253 | 262.6708338 | 23568.86757
48 |  | 20954.7833 | 8886.86065 | 16814.51154 |  | 227.6142375 |  | 5974.830369 |  | 288.0868118 |  | 0 | 0 | 0 | 16814.51154 | 227.6142375 | 20954.7833
49 |  | 18177.15126 | 11097.94834 | 14871.56415 |  | 165.7306907 |  | 6093.284714 |  | 744.5970491 |  | 0 | 0 | 0 | 14871.56415 | 165.7306907 | 18177.15126
50 |  | 15346.63483 | 13087.25161 | 13031.09156 |  | 94.6287097 |  | 6205.491548 |  | 1269.110977 |  | 0 | 0 | 0 | 13031.09156 | 94.6287097 | 15346.63483
51 |  | 12581.41116 | 14598.409 | 11297.52763 |  | 34.53984995 |  | 6311.180554 |  | 1712.381943 |  | 0 | 0 | 0 | 11297.52763 | 34.53984995 | 12581.41116
52 |  | 9992.489108 | 15426.23902 | 9675.048674 |  | 2.561962613 |  | 6410.097119 |  | 1948.280396 |  | 0 | 0 | 0 | 9675.048674 | 2.561962613 | 9992.489108
53 |  | 7670.742773 | 15459.17225 | 8167.563381 |  | 7.794124642 |  | 6502.002944 |  | 1909.683133 |  | 0 | 0 | 0 | 8167.563381 | 7.794124642 | 7670.742773
54 |  | 5677.763602 | 14702.26339 | 6778.703416 |  | 48.74756211 |  | 6586.676619 |  | 1607.572727 |  | 0 | 0 | 0 | 6778.703416 | 48.74756211 | 5677.763602
55 |  | 4041.822423 | 13275.00537 | 5511.814664 |  | 113.7692701 |  | 6663.91416 |  | 1127.912513 |  | 0 | 0 | 0 | 5511.814664 | 113.7692701 | 4041.822423
56 |  | 2759.164432 | 11384.72727 | 4369.949171 |  | 184.357791 |  | 6733.529492 |  | 607.186341 |  | 0 | 0 | 0 | 4369.949171 | 184.357791 | 2759.164432
57 |  | 1799.79881 | 9282.67461 | 3355.857791 |  | 240.4276709 |  | 6795.354908 |  | 193.5630844 |  | 0 | 0 | 0 | 3355.857791 | 240.4276709 | 1799.79881
58 |  | 1116.146898 | 7214.198476 | 2471.98356 |  | 266.0246302 |  | 6849.241464 |  | 4.736254211 |  | 0 | 0 | 0 | 2471.98356 | 266.0246302 | 1116.146898
59 |  | 652.5586997 | 5375.634481 | 1720.455806 |  | 253.8652391 |  | 6895.059342 |  | 94.43516157 |  | 0 | 0 | 0 | 1720.455806 | 253.8652391 | 652.5586997
60 |  | 353.854095 | 3888.147667 | 1103.085028 |  | 207.4093644 |  | 6932.698164 |  | 437.13663 |  | 0 | 0 | 0 | 1103.085028 | 207.4093644 | 353.854095
61 |  | 171.6141591 | 2793.744039 | 621.3585238 |  | 139.8756899 |  | 6962.067255 |  | 935.327431 |  | 0 | 0 | 0 | 621.3585238 | 139.8756899 | 171.6141591
62 |  | 67.7514434 | 2072.267795 | 276.4368163 |  | 70.48043509 |  | 6983.09586 |  | 1447.250969 |  | 0 | 0 | 0 | 276.4368163 | 70.48043509 | 67.7514434
63 |  | 15.6839604 | 1672.338567 | 69.15085169 |  | 18.96951867 |  | 6995.733322 |  | 1827.243098 |  | 0 | 0 | 0 | 69.15085169 | 18.96951867 | 15.6839604
64 |  | 0 | 1545.496113 | 0 |  | 0 |  | 6999.949195 |  | 1967.1798 |  | 0 | 0 | 0 | 0 | 0 | 0
65 |  | 15.6839604 | 1672.338567 | 69.15085169 |  | 18.96951867 |  | 6995.733322 |  | 1827.243098 |  | 0 | 0 | 0 | 69.15085169 | 18.96951867 | 15.6839604
66 |  | 67.7514434 | 2072.267795 | 276.4368163 |  | 70.48043509 |  | 6983.09586 |  | 1447.250969 |  | 0 | 0 | 0 | 276.4368163 | 70.48043509 | 67.7514434
67 |  | 171.6141591 | 2793.744039 | 621.3585238 |  | 139.8756899 |  | 6962.067255 |  | 935.327431 |  | 0 | 0 | 0 | 621.3585238 | 139.8756899 | 171.6141591
68 |  | 353.854095 | 3888.147667 | 1103.085028 |  | 207.4093644 |  | 6932.698164 |  | 437.13663 |  | 0 | 0 | 0 | 1103.085028 | 207.4093644 | 353.854095
69 |  | 652.5586997 | 5375.634481 | 1720.455806 |  | 253.8652391 |  | 6895.059342 |  | 94.43516157 |  | 0 | 0 | 0 | 1720.455806 | 253.8652391 | 652.5586997
70 |  | 1116.146898 | 7214.198476 | 2471.98356 |  | 266.0246302 |  | 6849.241464 |  | 4.736254211 |  | 0 | 0 | 0 | 2471.98356 | 266.0246302 | 1116.146898
71 |  | 1799.79881 | 9282.67461 | 3355.857791 |  | 240.4276709 |  | 6795.354908 |  | 193.5630844 |  | 0 | 0 | 0 | 3355.857791 | 240.4276709 | 1799.79881
72 |  | 2759.164432 | 11384.72727 | 4369.949171 |  | 184.357791 |  | 6733.529492 |  | 607.186341 |  | 0 | 0 | 0 | 4369.949171 | 184.357791 | 2759.164432
73 |  | 4041.822423 | 13275.00537 | 5511.814664 |  | 113.7692701 |  | 6663.91416 |  | 1127.912513 |  | 0 | 0 | 0 | 5511.814664 | 113.7692701 | 4041.822423
74 |  | 5677.763602 | 14702.26339 | 6778.703416 |  | 48.74756211 |  | 6586.676619 |  | 1607.572727 |  | 0 | 0 | 0 | 6778.703416 | 48.74756211 | 5677.763602
75 |  | 7670.742773 | 15459.17225 | 8167.563381 |  | 7.794124642 |  | 6502.002944 |  | 1909.683133 |  | 0 | 0 | 0 | 8167.563381 | 7.794124642 | 7670.742773
76 |  | 9992.489108 | 15426.23902 | 9675.048674 |  | 2.561962613 |  | 6410.097119 |  | 1948.280396 |  | 0 | 0 | 0 | 9675.048674 | 2.561962613 | 9992.489108
77 |  | 12581.41116 | 14598.409 | 11297.52763 |  | 34.53984995 |  | 6311.180554 |  | 1712.381943 |  | 0 | 0 | 0 | 11297.52763 | 34.53984995 | 12581.41116
78 |  | 15346.63483 | 13087.25161 | 13031.09156 |  | 94.6287097 |  | 6205.491548 |  | 1269.110977 |  | 0 | 0 | 0 | 13031.09156 | 94.6287097 | 15346.63483
79 |  | 18177.15126 | 11097.94834 | 14871.56415 |  | 165.7306907 |  | 6093.284714 |  | 744.5970491 |  | 0 | 0 | 0 | 14871.56415 | 165.7306907 | 18177.15126
80 |  | 20954.7833 | 8886.86065 | 16814.51154 |  | 227.6142375 |  | 5974.830369 |  | 288.0868118 |  | 0 | 0 | 0 | 16814.51154 | 227.6142375 | 20954.7833
81 |  | 23568.86757 | 6710.438599 | 18855.253 |  | 262.6708338 |  | 5850.41388 |  | 29.47695667 |  | 0 | 0 | 0 | 18855.253 | 262.6708338 | 23568.86757
82 |  | 25930.19476 | 4778.262026 | 20988.87221 |  | 260.9253781 |  | 5720.334977 |  | 42.35305087 |  | 0 | 0 | 0 | 20988.87221 | 260.9253781 | 25930.19476
83 |  | 27981.93593 | 3221.539559 | 23210.22909 |  | 222.8745273 |  | 5584.907031 |  | 323.0512947 |  | 0 | 0 | 0 | 23210.22909 | 222.8745273 | 27981.93593
84 |  | 29705.95121 | 2083.865597 | 25513.97221 |  | 159.3453763 |  | 5444.4563 |  | 791.7010296 |  | 0 | 0 | 0 | 25513.97221 | 159.3453763 | 29705.95121
85 |  | 31123.85028 | 1334.746184 | 27894.55163 |  | 88.41468621 |  | 5299.321142 |  | 1314.951357 |  | 0 | 0 | 0 | 27894.55163 | 88.41468621 | 31123.85028
86 |  | 32293.19999 | 900.135204 | 30346.23233 |  | 30.26527288 |  | 5149.851202 |  | 1743.915174 |  | 0 | 0 | 0 | 30346.23233 | 30.26527288 | 32293.19999
87 |  | 33300.10047 | 699.7368476 | 32863.10801 |  | 1.443132005 |  | 4996.406563 |  | 1956.533924 |  | 0 | 0 | 0 | 32863.10801 | 1.443132005 | 33300.10047
88 |  | 34249.78879 | 679.3745391 | 35439.11529 |  | 10.14939567 |  | 4839.356889 |  | 1892.308477 |  | 0 | 0 | 0 | 35439.11529 | 10.14939567 | 34249.78879
89 |  | 35256.90701 | 828.6750287 | 38068.04833 |  | 53.9067594 |  | 4679.080526 |  | 1569.513719 |  | 0 | 0 | 0 | 38068.04833 | 53.9067594 | 35256.90701
90 |  | 36436.64916 | 1179.069943 | 40743.57382 |  | 120.2643813 |  | 4515.963594 |  | 1079.998569 |  | 0 | 0 | 0 | 40743.57382 | 120.2643813 | 36436.64916
91 |  | 37897.34818 | 1783.276502 | 43459.24617 |  | 190.3406791 |  | 4350.399055 |  | 563.0510284 |  | 0 | 0 | 0 | 43459.24617 | 190.3406791 | 37897.34818
92 |  | 39734.40553 | 2683.187421 | 46208.5231 |  | 244.1959483 |  | 4182.785769 |  | 165.7647872 |  | 0 | 0 | 0 | 46208.5231 | 244.1959483 | 39734.40553
93 |  | 42025.01835 | 3876.797326 | 48984.78135 |  | 266.5060608 |  | 4013.527531 |  | 1.184777111 |  | 0 | 0 | 0 | 48984.78135 | 266.5060608 | 42025.01835
94 |  | 44823.06171 | 5295.337497 | 51781.33267 |  | 250.9228352 |  | 3843.032099 |  | 116.1410518 |  | 0 | 0 | 0 | 51781.33267 | 250.9228352 | 44823.06171
95 |  | 48153.76011 | 6799.008928 | 54591.43993 |  | 201.8803659 |  | 3671.710211 |  | 477.9236332 |  | 0 | 0 | 0 | 54591.43993 | 201.8803659 | 48153.76011
96 |  | 52008.33333 | 8194.380938 | 57408.33333 |  | 133.3333333 |  | 3499.974597 |  | 983.5898999 |  | 0 | 0 | 0 | 57408.33333 | 133.3333333 | 52008.33333
97 |  | 56339.43351 | 9270.179927 | 60225.22674 |  | 64.78630077 |  | 3328.238984 |  | 1489.256167 |  | 0 | 0 | 0 | 60225.22674 | 64.78630077 | 56339.43351
98 |  | 61058.67458 | 9842.653712 | 63035.334 |  | 15.74383142 |  | 3156.917096 |  | 1851.038748 |  | 0 | 0 | 0 | 63035.334 | 15.74383142 | 61058.67458
99 |  | 66037.69597 | 9798.565726 | 65831.88532 |  | 0.1606058393 |  | 2986.421664 |  | 1965.995023 |  | 0 | 0 | 0 | 65831.88532 | 0.1606058393 | 66037.69597
100 |  | 71113.89782 | 9124.077518 | 68608.14357 |  | 22.47071836 |  | 2817.163426 |  | 1801.415013 |  | 0 | 0 | 0 | 68608.14357 | 22.47071836 | 71113.89782
101 |  | 76101.26213 | 7911.299724 | 71357.42049 |  | 76.32598754 |  | 2649.55014 |  | 1404.128771 |  | 0 | 0 | 0 | 71357.42049 | 76.32598754 | 76101.26213
102 |  | 80805.68373 | 6340.170302 | 74073.09285 |  | 146.4022854 |  | 2483.985601 |  | 887.1812307 |  | 0 | 0 | 0 | 74073.09285 | 146.4022854 | 80805.68373
103 |  | 85043.21687 | 4639.920444 | 76748.61833 |  | 212.7599073 |  | 2320.868668 |  | 397.6660806 |  | 0 | 0 | 0 | 76748.61833 | 212.7599073 | 85043.21687
104 |  | 88658.85959 | 3039.867518 | 79377.55138 |  | 256.517271 |  | 2160.592305 |  | 74.871323 |  | 0 | 0 | 0 | 79377.55138 | 256.517271 | 88658.85959
105 |  | 91543.16153 | 1722.096293 | 81953.55866 |  | 265.2235347 |  | 2003.542631 |  | 10.64587548 |  | 0 | 0 | 0 | 81953.55866 | 265.2235347 | 91543.16153
106 |  | 93644.15712 | 787.9655041 | 84470.43433 |  | 236.4013938 |  | 1850.097993 |  | 223.2646255 |  | 0 | 0 | 0 | 84470.43433 | 236.4013938 | 93644.15712
107 |  | 94972.86069 | 246.4871198 | 86922.11504 |  | 178.2519805 |  | 1700.628052 |  | 652.2284427 |  | 0 | 0 | 0 | 86922.11504 | 178.2519805 | 94972.86069
108 |  | 95601.64895 | 26.56868094 | 89302.69446 |  | 107.3212904 |  | 1555.492895 |  | 1175.47877 |  | 0 | 0 | 0 | 89302.69446 | 107.3212904 | 95601.64895
109 |  | 95656.04642 | 8.589637396 | 91606.43757 |  | 43.79213935 |  | 1415.042164 |  | 1644.128505 |  | 0 | 0 | 0 | 91606.43757 | 43.79213935 | 95656.04642
110 |  | 95301.44915 | 65.62865962 | 93827.79446 |  | 5.741288569 |  | 1279.614218 |  | 1924.826749 |  | 0 | 0 | 0 | 93827.79446 | 5.741288569 | 95301.44915
111 |  | 94726.94953 | 102.3040898 | 95961.41367 |  | 3.995832907 |  | 1149.535315 |  | 1937.702843 |  | 0 | 0 | 0 | 95961.41367 | 3.995832907 | 94726.94953
112 |  | 94128.55004 | 80.26834476 | 98002.15513 |  | 39.05242918 |  | 1025.118826 |  | 1679.092988 |  | 0 | 0 | 0 | 98002.15513 | 39.05242918 | 94128.55004
113 |  | 93693.69831 | 23.56695674 | 99945.10252 |  | 100.935976 |  | 906.6644807 |  | 1222.582751 |  | 0 | 0 | 0 | 99945.10252 | 100.935976 | 93693.69831
114 |  | 93588.38792 | 3.11569446 | 101785.5751 |  | 172.037957 |  | 794.4576471 |  | 698.0688233 |  | 0 | 0 | 0 | 101785.5751 | 172.037957 | 93588.38792
115 |  | 93947.27315 | 105.7197969 | 103519.139 |  | 232.1268167 |  | 688.7686408 |  | 254.7978567 |  | 0 | 0 | 0 | 103519.139 | 232.1268167 | 93947.27315
116 |  | 94866.5774 | 397.5846951 | 105141.618 |  | 264.1047041 |  | 589.8520758 |  | 18.89940413 |  | 0 | 0 | 0 | 105141.618 | 264.1047041 | 94866.5774
117 |  | 96399.21292 | 893.8524321 | 106649.1033 |  | 258.872542 |  | 497.9462509 |  | 57.49666708 |  | 0 | 0 | 0 | 106649.1033 | 258.872542 | 96399.21292
118 |  | 98551.54596 | 1543.893892 | 108037.9633 |  | 217.9191046 |  | 413.2725753 |  | 359.607073 |  | 0 | 0 | 0 | 108037.9633 | 217.9191046 | 98551.54596
119 |  | 101281.5823 | 2237.419477 | 109304.852 |  | 152.8973966 |  | 336.0350351 |  | 839.2672872 |  | 0 | 0 | 0 | 109304.852 | 152.8973966 | 101281.5823
120 |  | 104498.8539 | 2830.288658 | 110446.7175 |  | 82.30887568 |  | 266.4197026 |  | 1359.993459 |  | 0 | 0 | 0 | 110446.7175 | 82.30887568 | 104498.8539
121 |  | 108066.744 | 3182.987906 | 111460.8089 |  | 26.2389958 |  | 204.5942869 |  | 1773.616715 |  | 0 | 0 | 0 | 111460.8089 | 26.2389958 | 108066.744
122 |  | 111808.1869 | 3200.819267 | 112344.6831 |  | 0.6420364437 |  | 150.7077311 |  | 1962.443546 |  | 0 | 0 | 0 | 112344.6831 | 0.6420364437 | 111808.1869
123 |  | 115515.4977 | 2864.047282 | 113096.2109 |  | 12.80142758 |  | 104.8898525 |  | 1872.744638 |  | 0 | 0 | 0 | 113096.2109 | 12.80142758 | 115515.4977
124 |  | 118964.5092 | 2238.845383 | 113713.5816 |  | 59.25730226 |  | 67.25103048 |  | 1530.04317 |  | 0 | 0 | 0 | 113713.5816 | 59.25730226 | 118964.5092
125 |  | 121932.3382 | 1465.150898 | 114195.3081 |  | 126.7909768 |  | 37.88194018 |  | 1031.852369 |  | 0 | 0 | 0 | 114195.3081 | 126.7909768 | 121932.3382
126 |  | 124217.1789 | 723.9989849 | 114540.2299 |  | 196.1862316 |  | 16.85333433 |  | 519.9288307 |  | 0 | 0 | 0 | 114540.2299 | 196.1862316 | 124217.1789
127 |  | 125657.7891 | 192.7305667 | 114747.5158 |  | 247.697148 |  | 4.215872683 |  | 139.9367023 |  | 0 | 0 | 0 | 114747.5158 | 247.697148 | 125657.7891
128 |  | 126150 | 0 | 114816.6667 |  | 266.6666667 |  | 0 |  | 0 |  | 0 | 0 | 0 | 114816.6667 | 266.6666667 | 126150
129 |  | 125657.7891 | 192.7305667 | 114747.5158 |  | 247.697148 |  | 4.215872683 |  | 139.9367023 |  | 0 | 0 | 0 | 114747.5158 | 247.697148 | 125657.7891
130 |  | 124217.1789 | 723.9989849 | 114540.2299 |  | 196.1862316 |  | 16.85333433 |  | 519.9288307 |  | 0 | 0 | 0 | 114540.2299 | 196.1862316 | 124217.1789
131 |  | 121932.3382 | 1465.150898 | 114195.3081 |  | 126.7909768 |  | 37.88194018 |  | 1031.852369 |  | 0 | 0 | 0 | 114195.3081 | 126.7909768 | 121932.3382
132 |  | 118964.5092 | 2238.845383 | 113713.5816 |  | 59.25730226 |  | 67.25103048 |  | 1530.04317 |  | 0 | 0 | 0 | 113713.5816 | 59.25730226 | 118964.5092
133 |  | 115515.4977 | 2864.047282 | 113096.2109 |  | 12.80142758 |  | 104.8898525 |  | 1872.744638 |  | 0 | 0 | 0 | 113096.2109 | 12.80142758 | 115515.4977
134 |  | 111808.1869 | 3200.819267 | 112344.6831 |  | 0.6420364437 |  | 150.7077311 |  | 1962.443546 |  | 0 | 0 | 0 | 112344.6831 | 0.6420364437 | 111808.1869
135 |  | 108066.744 | 3182.987906 | 111460.8089 |  | 26.2389958 |  | 204.5942869 |  | 1773.616715 |  | 0 | 0 | 0 | 111460.8089 | 26.2389958 | 108066.744
136 |  | 104498.8539 | 2830.288658 | 110446.7175 |  | 82.30887568 |  | 266.4197026 |  | 1359.993459 |  | 0 | 0 | 0 | 110446.7175 | 82.30887568 | 104498.8539
137 |  | 101281.5823 | 2237.419477 | 109304.852 |  | 152.8973966 |  | 336.0350351 |  | 839.2672872 |  | 0 | 0 | 0 | 109304.852 | 152.8973966 | 101281.5823
138 |  | 98551.54596 | 1543.893892 | 108037.9633 |  | 217.9191046 |  | 413.2725753 |  | 359.607073 |  | 0 | 0 | 0 | 108037.9633 | 217.9191046 | 98551.54596
139 |  | 96399.21292 | 893.8524321 | 106649.1033 |  | 258.872542 |  | 497.9462509 |  | 57.49666708 |  | 0 | 0 | 0 | 106649.1033 | 258.872542 | 96399.21292
140 |  | 94866.5774 | 397.5846951 | 105141.618 |  | 264.1047041 |  | 589.8520758 |  | 18.89940413 |  | 0 | 0 | 0 | 105141.618 | 264.1047041 | 94866.5774
141 |  | 93947.27315 | 105.7197969 | 103519.139 |  | 232.1268167 |  | 688.7686408 |  | 254.7978567 |  | 0 | 0 | 0 | 103519.139 | 232.1268167 | 93947.27315
142 |  | 93588.38792 | 3.11569446 | 101785.5751 |  | 172.037957 |  | 794.4576471 |  | 698.0688233 |  | 0 | 0 | 0 | 101785.5751 | 172.037957 | 93588.38792
143 |  | 93693.69831 | 23.56695674 | 99945.10252 |  | 100.935976 |  | 906.6644807 |  | 1222.582751 |  | 0 | 0 | 0 | 99945.10252 | 100.935976 | 93693.69831
144 |  | 94128.55004 | 80.26834476 | 98002.15513 |  | 39.05242918 |  | 1025.118826 |  | 1679.092988 |  | 0 | 0 | 0 | 98002.15513 | 39.05242918 | 94128.55004
145 |  | 94726.94953 | 102.3040898 | 95961.41367 |  | 3.995832907 |  | 1149.535315 |  | 1937.702843 |  | 0 | 0 | 0 | 95961.41367 | 3.995832907 | 94726.94953
146 |  | 95301.44915 | 65.62865962 | 93827.79446 |  | 5.741288569 |  | 1279.614218 |  | 1924.826749 |  | 0 | 0 | 0 | 93827.79446 | 5.741288569 | 95301.44915
147 |  | 95656.04642 | 8.589637396 | 91606.43757 |  | 43.79213935 |  | 1415.042164 |  | 1644.128505 |  | 0 | 0 | 0 | 91606.43757 | 43.79213935 | 95656.04642
148 |  | 95601.64895 | 26.56868094 | 89302.69446 |  | 107.3212904 |  | 1555.492895 |  | 1175.47877 |  | 0 | 0 | 0 | 89302.69446 | 107.3212904 | 95601.64895
149 |  | 94972.86069 | 246.4871198 | 86922.11504 |  | 178.2519805 |  | 1700.628052 |  | 652.2284427 |  | 0 | 0 | 0 | 86922.11504 | 178.2519805 | 94972.86069
150 |  | 93644.15712 | 787.9655041 | 84470.43433 |  | 236.4013938 |  | 1850.097993 |  | 223.2646255 |  | 0 | 0 | 0 | 84470.43433 | 236.4013938 | 93644.15712
151 |  | 91543.16153 | 1722.096293 | 81953.55866 |  | 265.2235347 |  | 2003.542631 |  | 10.64587548 |  | 0 | 0 | 0 | 81953.55866 | 265.2235347 | 91543.16153
152 |  | 88658.85959 | 3039.867518 | 79377.55138 |  | 256.517271 |  | 2160.592305 |  | 74.871323 |  | 0 | 0 | 0 | 79377.55138 | 256.517271 | 88658.85959
153 |  | 85043.21687 | 4639.920444 | 76748.61833 |  | 212.7599073 |  | 2320.868668 |  | 397.6660806 |  | 0 | 0 | 0 | 76748.61833 | 212.7599073 | 85043.21687
154 |  | 80805.68373 | 6340.170302 | 74073.09285 |  | 146.4022854 |  | 2483.985601 |  | 887.1812307 |  | 0 | 0 | 0 | 74073.09285 | 146.4022854 | 80805.68373
155 |  | 76101.26213 | 7911.299724 | 71357.42049 |  | 76.32598754 |  | 2649.55014 |  | 1404.128771 |  | 0 | 0 | 0 | 71357.42049 | 76.32598754 | 76101.26213
156 |  | 71113.89782 | 9124.077518 | 68608.14357 |  | 22.47071836 |  | 2817.163426 |  | 1801.415013 |  | 0 | 0 | 0 | 68608.14357 | 22.47071836 | 71113.89782
157 |  | 66037.69597 | 9798.565726 | 65831.88532 |  | 0.1606058393 |  | 2986.421664 |  | 1965.995023 |  | 0 | 0 | 0 | 65831.88532 | 0.1606058393 | 66037.69597
158 |  | 61058.67458 | 9842.653712 | 63035.334 |  | 15.74383142 |  | 3156.917096 |  | 1851.038748 |  | 0 | 0 | 0 | 63035.334 | 15.74383142 | 61058.67458
159 |  | 56339.43351 | 9270.179927 | 60225.22674 |  | 64.78630077 |  | 3328.238984 |  | 1489.256167 |  | 0 | 0 | 0 | 60225.22674 | 64.78630077 | 56339.43351
160 |  | 52008.33333 | 8194.380938 | 57408.33333 |  | 133.3333333 |  | 3499.974597 |  | 983.5898999 |  | 0 | 0 | 0 | 57408.33333 | 133.3333333 | 52008.33333
161 |  | 48153.76011 | 6799.008928 | 54591.43993 |  | 201.8803659 |  | 3671.710211 |  | 477.9236332 |  | 0 | 0 | 0 | 54591.43993 | 201.8803659 | 48153.76011
162 |  | 44823.06171 | 5295.337497 | 51781.33267 |  | 250.9228352 |  | 3843.032099 |  | 116.1410518 |  | 0 | 0 | 0 | 51781.33267 | 250.9228352 | 44823.06171
163 |  | 42025.01835 | 3876.797326 | 48984.78135 |  | 266.5060608 |  | 4013.527531 |  | 1.184777111 |  | 0 | 0 | 0 | 48984.78135 | 266.5060608 | 42025.01835
164 |  | 39734.40553 | 2683.187421 | 46208.5231 |  | 244.1959483 |  | 4182.785769 |  | 165.7647872 |  | 0 | 0 | 0 | 46208.5231 | 244.1959483 | 39734.40553
165 |  | 37897.34818 | 1783.276502 | 43459.24617 |  | 190.3406791 |  | 4350.399055 |  | 563.0510284 |  | 0 | 0 | 0 | 43459.24617 | 190.3406791 | 37897.34818
166 |  | 36436.64916 | 1179.069943 | 40743.57382 |  | 120.2643813 |  | 4515.963594 |  | 1079.998569 |  | 0 | 0 | 0 | 40743.57382 | 120.2643813 | 36436.64916
167 |  | 35256.90701 | 828.6750287 | 38068.04833 |  | 53.9067594 |  | 4679.080526 |  | 1569.513719 |  | 0 | 0 | 0 | 38068.04833 | 53.9067594 | 35256.90701
168 |  | 34249.78879 | 679.3745391 | 35439.11529 |  | 10.14939567 |  | 4839.356889 |  | 1892.308477 |  | 0 | 0 | 0 | 35439.11529 | 10.14939567 | 34249.78879
169 |  | 33300.10047 | 699.7368476 | 32863.10801 |  | 1.443132005 |  | 4996.406563 |  | 1956.533924 |  | 0 | 0 | 0 | 32863.10801 | 1.443132005 | 33300.10047
170 |  | 32293.19999 | 900.135204 | 30346.23233 |  | 30.26527288 |  | 5149.851202 |  | 1743.915174 |  | 0 | 0 | 0 | 30346.23233 | 30.26527288 | 32293.19999
171 |  | 31123.85028 | 1334.746184 | 27894.55163 |  | 88.41468621 |  | 5299.321142 |  | 1314.951357 |  | 0 | 0 | 0 | 27894.55163 | 88.41468621 | 31123.85028
172 |  | 29705.95121 | 2083.865597 | 25513.97221 |  | 159.3453763 |  | 5444.4563 |  | 791.7010296 |  | 0 | 0 | 0 | 25513.97221 | 159.3453763 | 29705.95121
173 |  | 27981.93593 | 3221.539559 | 23210.22909 |  | 222.8745273 |  | 5584.907031 |  | 323.0512947 |  | 0 | 0 | 0 | 23210.22909 | 222.8745273 | 27981.93593
174 |  | 25930.19476 | 4778.262026 | 20988.87221 |  | 260.9253781 |  | 5720.334977 |  | 42.35305087 |  | 0 | 0 | 0 | 20988.87221 | 260.9253781 | 25930.19476
175 |  | 23568.86757 | 6710.438599 | 18855.253 |  | 262.6708338 |  | 5850.41388 |  | 29.47695667 |  | 0 | 0 | 0 | 18855.253 | 262.6708338 | 23568.86757
176 |  | 20954.7833 | 8886.86065 | 16814.51154 |  | 227.6142375 |  | 5974.830369 |  | 288.0868118 |  | 0 | 0 | 0 | 16814.51154 | 227.6142375 | 20954.7833
177 |  | 18177.15126 | 11097.94834 | 14871.56415 |  | 165.7306907 |  | 6093.284714 |  | 744.5970491 |  | 0 | 0 | 0 | 14871.56415 | 165.7306907 | 18177.15126
178 |  | 15346.63483 | 13087.25161 | 13031.09156 |  | 94.6287097 |  | 6205.491548 |  | 1269.110977 |  | 0 | 0 | 0 | 13031.09156 | 94.6287097 | 15346.63483
179 |  | 12581.41116 | 14598.409 | 11297.52763 |  | 34.53984995 |  | 6311.180554 |  | 1712.381943 |  | 0 | 0 | 0 | 11297.52763 | 34.53984995 | 12581.41116
180 |  | 9992.489108 | 15426.23902 | 9675.048674 |  | 2.561962613 |  | 6410.097119 |  | 1948.280396 |  | 0 | 0 | 0 | 9675.048674 | 2.561962613 | 9992.489108
181 |  | 7670.742773 | 15459.17225 | 8167.563381 |  | 7.794124642 |  | 6502.002944 |  | 1909.683133 |  | 0 | 0 | 0 | 8167.563381 | 7.794124642 | 7670.742773
182 |  | 5677.763602 | 14702.26339 | 6778.703416 |  | 48.74756211 |  | 6586.676619 |  | 1607.572727 |  | 0 | 0 | 0 | 6778.703416 | 48.74756211 | 5677.763602
183 |  | 4041.822423 | 13275.00537 | 5511.814664 |  | 113.7692701 |  | 6663.91416 |  | 1127.912513 |  | 0 | 0 | 0 | 5511.814664 | 113.7692701 | 4041.822423
184 |  | 2759.164432 | 11384.72727 | 4369.949171 |  | 184.357791 |  | 6733.529492 |  | 607.186341 |  | 0 | 0 | 0 | 4369.949171 | 184.357791 | 2759.164432
185 |  | 1799.79881 | 9282.67461 | 3355.857791 |  | 240.4276709 |  | 6795.354908 |  | 193.5630844 |  | 0 | 0 | 0 | 3355.857791 | 240.4276709 | 1799.79881
186 |  | 1116.146898 | 7214.198476 | 2471.98356 |  | 266.0246302 |  | 6849.241464 |  | 4.736254211 |  | 0 | 0 | 0 | 2471.98356 | 266.0246302 | 1116.146898
187 |  | 652.5586997 | 5375.634481 | 1720.455806 |  | 253.8652391 |  | 6895.059342 |  | 94.43516157 |  | 0 | 0 | 0 | 1720.455806 | 253.8652391 | 652.5586997
188 |  | 353.854095 | 3888.147667 | 1103.085028 |  | 207.4093644 |  | 6932.698164 |  | 437.13663 |  | 0 | 0 | 0 | 1103.085028 | 207.4093644 | 353.854095
189 |  | 171.6141591 | 2793.744039 | 621.3585238 |  | 139.8756899 |  | 6962.067255 |  | 935.327431 |  | 0 | 0 | 0 | 621.3585238 | 139.8756899 | 171.6141591
190 |  | 67.7514434 | 2072.267795 | 276.4368163 |  | 70.48043509 |  | 6983.09586 |  | 1447.250969 |  | 0 | 0 | 0 | 276.4368163 | 70.48043509 | 67.7514434
191 |  | 15.6839604 | 1672.338567 | 69.15085169 |  | 18.96951867 |  | 6995.733322 |  | 1827.243098 |  | 0 | 0 | 0 | 69.15085169 | 18.96951867 | 15.6839604
192 |  | 0 | 1545.496113 | 0 |  | 0 |  | 6999.949195 |  | 1967.1798 |  | 0 | 0 | 0 | 0 | 0 | 0
193 |  | 15.6839604 | 1672.338567 | 69.15085169 |  | 18.96951867 |  | 6995.733322 |  | 1827.243098 |  | 0 | 0 | 0 | 69.15085169 | 18.96951867 | 15.6839604
194 |  | 67.7514434 | 2072.267795 | 276.4368163 |  | 70.48043509 |  | 6983.09586 |  | 1447.250969 |  | 0 | 0 | 0 | 276.4368163 | 70.48043509 | 67.7514434
195 |  | 171.6141591 | 2793.744039 | 621.3585238 |  | 139.8756899 |  | 6962.067255 |  | 935.327431 |  | 0 | 0 | 0 | 621.3585238 | 139.8756899 | 171.6141591
196 |  | 353.854095 | 3888.147667 | 1103.085028 |  | 207.4093644 |  | 6932.698164 |  | 437.13663 |  | 0 | 0 | 0 | 1103.085028 | 207.4093644 | 353.854095
197 |  | 652.5586997 | 5375.634481 | 1720.455806 |  | 253.8652391 |  | 6895.059342 |  | 94.43516157 |  | 0 | 0 | 0 | 1720.455806 | 253.8652391 | 652.5586997
198 |  | 1116.146898 | 7214.198476 | 2471.98356 |  | 266.0246302 |  | 6849.241464 |  | 4.736254211 |  | 0 | 0 | 0 | 2471.98356 | 266.0246302 | 1116.146898
199 |  | 1799.79881 | 9282.67461 | 3355.857791 |  | 240.4276709 |  | 6795.354908 |  | 193.5630844 |  | 0 | 0 | 0 | 3355.857791 | 240.4276709 | 1799.79881
200 |  | 2759.164432 | 11384.72727 | 4369.949171 |  | 184.357791 |  | 6733.529492 |  | 607.186341 |  | 0 | 0 | 0 | 4369.949171 | 184.357791 | 2759.164432
201 |  | 4041.822423 | 13275.00537 | 5511.814664 |  | 113.7692701 |  | 6663.91416 |  | 1127.912513 |  | 0 | 0 | 0 | 5511.814664 | 113.7692701 | 4041.822423
202 |  | 5677.763602 | 14702.26339 | 6778.703416 |  | 48.74756211 |  | 6586.676619 |  | 1607.572727 |  | 0 | 0 | 0 | 6778.703416 | 48.74756211 | 5677.763602
203 |  | 7670.742773 | 15459.17225 | 8167.563381 |  | 7.794124642 |  | 6502.002944 |  | 1909.683133 |  | 0 | 0 | 0 | 8167.563381 | 7.794124642 | 7670.742773
204 |  | 9992.489108 | 15426.23902 | 9675.048674 |  | 2.561962613 |  | 6410.097119 |  | 1948.280396 |  | 0 | 0 | 0 | 9675.048674 | 2.561962613 | 9992.489108
205 |  | 12581.41116 | 14598.409 | 11297.52763 |  | 34.53984995 |  | 6311.180554 |  | 1712.381943 |  | 0 | 0 | 0 | 11297.52763 | 34.53984995 | 12581.41116
206 |  | 15346.63483 | 13087.25161 | 13031.09156 |  | 94.6287097 |  | 6205.491548 |  | 1269.110977 |  | 0 | 0 | 0 | 13031.09156 | 94.6287097 | 15346.63483
207 |  | 18177.15126 | 11097.94834 | 14871.56415 |  | 165.7306907 |  | 6093.284714 |  | 744.5970491 |  | 0 | 0 | 0 | 14871.56415 | 165.7306907 | 18177.15126
208 |  | 20954.7833 | 8886.86065 | 16814.51154 |  | 227.6142375 |  | 5974.830369 |  | 288.0868118 |  | 0 | 0 | 0 | 16814.51154 | 227.6142375 | 20954.7833
209 |  | 23568.86757 | 6710.438599 | 18855.253 |  | 262.6708338 |  | 5850.41388 |  | 29.47695667 |  | 0 | 0 | 0 | 18855.253 | 262.6708338 | 23568.86757
210 |  | 25930.19476 | 4778.262026 | 20988.87221 |  | 260.9253781 |  | 5720.334977 |  | 42.35305087 |  | 0 | 0 | 0 | 20988.87221 | 260.9253781 | 25930.19476
211 |  | 27981.93593 | 3221.539559 | 23210.22909 |  | 222.8745273 |  | 5584.907031 |  | 323.0512947 |  | 0 | 0 | 0 | 23210.22909 | 222.8745273 | 27981.93593
212 |  | 29705.95121 | 2083.865597 | 25513.97221 |  | 159.3453763 |  | 5444.4563 |  | 791.7010296 |  | 0 | 0 | 0 | 25513.97221 | 159.3453763 | 29705.95121
213 |  | 31123.85028 | 1334.746184 | 27894.55163 |  | 88.41468621 |  | 5299.321142 |  | 1314.951357 |  | 0 | 0 | 0 | 27894.55163 | 88.41468621 | 31123.85028
214 |  | 32293.19999 | 900.135204 | 30346.23233 |  | 30.26527288 |  | 5149.851202 |  | 1743.915174 |  | 0 | 0 | 0 | 30346.23233 | 30.26527288 | 32293.19999
215 |  | 33300.10047 | 699.7368476 | 32863.10801 |  | 1.443132005 |  | 4996.406563 |  | 1956.533924 |  | 0 | 0 | 0 | 32863.10801 | 1.443132005 | 33300.10047
216 |  | 34249.78879 | 679.3745391 | 35439.11529 |  | 10.14939567 |  | 4839.356889 |  | 1892.308477 |  | 0 | 0 | 0 | 35439.11529 | 10.14939567 | 34249.78879
217 |  | 35256.90701 | 828.6750287 | 38068.04833 |  | 53.9067594 |  | 4679.080526 |  | 1569.513719 |  | 0 | 0 | 0 | 38068.04833 | 53.9067594 | 35256.90701
218 |  | 36436.64916 | 1179.069943 | 40743.57382 |  | 120.2643813 |  | 4515.963594 |  | 1079.998569 |  | 0 | 0 | 0 | 40743.57382 | 120.2643813 | 36436.64916
219 |  | 37897.34818 | 1783.276502 | 43459.24617 |  | 190.3406791 |  | 4350.399055 |  | 563.0510284 |  | 0 | 0 | 0 | 43459.24617 | 190.3406791 | 37897.34818
220 |  | 39734.40553 | 2683.187421 | 46208.5231 |  | 244.1959483 |  | 4182.785769 |  | 165.7647872 |  | 0 | 0 | 0 | 46208.5231 | 244.1959483 | 39734.40553
221 |  | 42025.01835 | 3876.797326 | 48984.78135 |  | 266.5060608 |  | 4013.527531 |  | 1.184777111 |  | 0 | 0 | 0 | 48984.78135 | 266.5060608 | 42025.01835
222 |  | 44823.06171 | 5295.337497 | 51781.33267 |  | 250.9228352 |  | 3843.032099 |  | 116.1410518 |  | 0 | 0 | 0 | 51781.33267 | 250.9228352 | 44823.06171
223 |  | 48153.76011 | 6799.008928 | 54591.43993 |  | 201.8803659 |  | 3671.710211 |  | 477.9236332 |  | 0 | 0 | 0 | 54591.43993 | 201.8803659 | 48153.76011
224 |  | 52008.33333 | 8194.380938 | 57408.33333 |  | 133.3333333 |  | 3499.974597 |  | 983.5898999 |  | 0 | 0 | 0 | 57408.33333 | 133.3333333 | 52008.33333
225 |  | 56339.43351 | 9270.179927 | 60225.22674 |  | 64.78630077 |  | 3328.238984 |  | 1489.256167 |  | 0 | 0 | 0 | 60225.22674 | 64.78630077 | 56339.43351
226 |  | 61058.67458 | 9842.653712 | 63035.334 |  | 15.74383142 |  | 3156.917096 |  | 1851.038748 |  | 0 | 0 | 0 | 63035.334 | 15.74383142 | 61058.67458
227 |  | 66037.69597 | 9798.565726 | 65831.88532 |  | 0.1606058393 |  | 2986.421664 |  | 1965.995023 |  | 0 | 0 | 0 | 65831.88532 | 0.1606058393 | 66037.69597
228 |  | 71113.89782 | 9124.077518 | 68608.14357 |  | 22.47071836 |  | 2817.163426 |  | 1801.415013 |  | 0 | 0 | 0 | 68608.14357 | 22.47071836 | 71113.89782
229 |  | 76101.26213 | 7911.299724 | 71357.42049 |  | 76.32598754 |  | 2649.55014 |  | 1404.128771 |  | 0 | 0 | 0 | 71357.42049 | 76.32598754 | 76101.26213
230 |  | 80805.68373 | 6340.170302 | 74073.09285 |  | 146.4022854 |  | 2483.985601 |  | 887.1812307 |  | 0 | 0 | 0 | 74073.09285 | 146.4022854 | 80805.68373
231 |  | 85043.21687 | 4639.920444 | 76748.61833 |  | 212.7599073 |  | 2320.868668 |  | 397.6660806 |  | 0 | 0 | 0 | 76748.61833 | 212.7599073 | 85043.21687
232 |  | 88658.85959 | 3039.867518 | 79377.55138 |  | 256.517271 |  | 2160.592305 |  | 74.871323 |  | 0 | 0 | 0 | 79377.55138 | 256.517271 | 88658.85959
233 |  | 91543.16153 | 1722.096293 | 81953.55866 |  | 265.2235347 |  | 2003.542631 |  | 10.64587548 |  | 0 | 0 | 0 | 81953.55866 | 265.2235347 | 91543.16153
234 |  | 93644.15712 | 787.9655041 | 84470.43433 |  | 236.4013938 |  | 1850.097993 |  | 223.2646255 |  | 0 | 0 | 0 | 84470.43433 | 236.4013938 | 93644.15712
235 |  | 94972.86069 | 246.4871198 | 86922.11504 |  | 178.2519805 |  | 1700.628052 |  | 652.2284427 |  | 0 | 0 | 0 | 86922.11504 | 178.2519805 | 94972.86069
236 |  | 95601.64895 | 26.56868094 | 89302.69446 |  | 107.3212904 |  | 1555.492895 |  | 1175.47877 |  | 0 | 0 | 0 | 89302.69446 | 107.3212904 | 95601.64895
237 |  | 95656.04642 | 8.589637396 | 91606.43757 |  | 43.79213935 |  | 1415.042164 |  | 1644.128505 |  | 0 | 0 | 0 | 91606.43757 | 43.79213935 | 95656.04642
238 |  | 95301.44915 | 65.62865962 | 93827.79446 |  | 5.741288569 |  | 1279.614218 |  | 1924.826749 |  | 0 | 0 | 0 | 93827.79446 | 5.741288569 | 95301.44915
239 |  | 94726.94953 | 102.3040898 | 95961.41367 |  | 3.995832907 |  | 1149.535315 |  | 1937.702843 |  | 0 | 0 | 0 | 95961.41367 | 3.995832907 | 94726.94953
240 |  | 94128.55004 | 80.26834476 | 98002.15513 |  | 39.05242918 |  | 1025.118826 |  | 1679.092988 |  | 0 | 0 | 0 | 98002.15513 | 39.05242918 | 94128.55004
241 |  | 93693.69831 | 23.56695674 | 99945.10252 |  | 100.935976 |  | 906.6644807 |  | 1222.582751 |  | 0 | 0 | 0 | 99945.10252 | 100.935976 | 93693.69831
242 |  | 93588.38792 | 3.11569446 | 101785.5751 |  | 172.037957 |  | 794.4576471 |  | 698.0688233 |  | 0 | 0 | 0 | 101785.5751 | 172.037957 | 93588.38792
243 |  | 93947.27315 | 105.7197969 | 103519.139 |  | 232.1268167 |  | 688.7686408 |  | 254.7978567 |  | 0 | 0 | 0 | 103519.139 | 232.1268167 | 93947.27315
244 |  | 94866.5774 | 397.5846951 | 105141.618 |  | 264.1047041 |  | 589.8520758 |  | 18.89940413 |  | 0 | 0 | 0 | 105141.618 | 264.1047041 | 94866.5774
245 |  | 96399.21292 | 893.8524321 | 106649.1033 |  | 258.872542 |  | 497.9462509 |  | 57.49666708 |  | 0 | 0 | 0 | 106649.1033 | 258.872542 | 96399.21292
246 |  | 98551.54596 | 1543.893892 | 108037.9633 |  | 217.9191046 |  | 413.2725753 |  | 359.607073 |  | 0 | 0 | 0 | 108037.9633 | 217.9191046 | 98551.54596
247 |  | 101281.5823 | 2237.419477 | 109304.852 |  | 152.8973966 |  | 336.0350351 |  | 839.2672872 |  | 0 | 0 | 0 | 109304.852 | 152.8973966 | 101281.5823
248 |  | 104498.8539 | 2830.288658 | 110446.7175 |  | 82.30887568 |  | 266.4197026 |  | 1359.993459 |  | 0 | 0 | 0 | 110446.7175 | 82.30887568 | 104498.8539
249 |  | 108066.744 | 3182.987906 | 111460.8089 |  | 26.2389958 |  | 204.5942869 |  | 1773.616715 |  | 0 | 0 | 0 | 111460.8089 | 26.2389958 | 108066.744
250 |  | 111808.1869 | 3200.819267 | 112344.6831 |  | 0.6420364437 |  | 150.7077311 |  | 1962.443546 |  | 0 | 0 | 0 | 112344.6831 | 0.6420364437 | 111808.1869
251 |  | 115515.4977 | 2864.047282 | 113096.2109 |  | 12.80142758 |  | 104.8898525 |  | 1872.744638 |  | 0 | 0 | 0 | 113096.2109 | 12.80142758 | 115515.4977
252 |  | 118964.5092 | 2238.845383 | 113713.5816 |  | 59.25730226 |  | 67.25103048 |  | 1530.04317 |  | 0 | 0 | 0 | 113713.5816 | 59.25730226 | 118964.5092
253 |  | 121932.3382 | 1465.150898 | 114195.3081 |  | 126.7909768 |  | 37.88194018 |  | 1031.852369 |  | 0 | 0 | 0 | 114195.3081 | 126.7909768 | 121932.3382
254 |  | 124217.1789 | 723.9989849 | 114540.2299 |  | 196.1862316 |  | 16.85333433 |  | 519.9288307 |  | 0 | 0 | 0 | 114540.2299 | 196.1862316 | 124217.1789
255 |  | 125657.7891 | 192.7305667 | 114747.5158 |  | 247.697148 |  | 4.215872683 |  | 139.9367023 |  | 0 | 0 | 0 | 114747.5158 | 247.697148 | 125657.7891