## Harmonics
Harmonic Simulation
Capacitor & Reactor Rating Input |  |  |  |  | Computed Values
|  | Cap Size : | 10 | kVar |  | C | = | 38.4955 | uF x3 | computed from rated capacitor
|  | Cap V rating : | 525 | V |  | L | = | 6.1414 | mH | computed from rated capacitor & reactor
|  | Cap Freq rating : | 50 | Hz | Icap (rated) |  | = | 10.9971 | A | rated current of capacitor
|  | Reactor Rating | 7 | % |  | F [res] | = | 188.9822 | Hz | resonance frequency for rated cap & reactor
Network Phase - Phase Value Input | [5 empty] | Irms (50Hz) | = | 9.3473 | A | 1st harmonic ampere of capacitor
|  | V_1st Harmonic : | 415 | V |  | Irms (550Hz) | = | 0.92537 | A | nth harmonic ampere of capacitor
|  | V_1st Freq : | 50 | Hz |  | Irms eff | = | 9.393 | A | total rms ampere of capacitor
[6 empty] | Vrms eff | = | 416.0829 | V | effective rms voltage value of network
|  | V_nth Harmonic : | 30 | V |  | V[L] 1st rms | = | 18.0344 | V | 1st harmonic voltage across reactor
|  | V_nth angle : | 180 | o |  | V[L] nth rms | = | 19.6392 | V | nth harmonic voltage across reactor
|  | V_nth Freq : | 550 | Hz |  | V[L] eff rms | = | 26.6634 | V | effective rms voltage across reactor
[6 empty] | V[C] 1st rms | = | 446.2366 | V | 1st harmonic P-P rms voltage across capacitor
[6 empty] | V[C] nth rms | = | 4.0161 | V | nth harmonic P-P rms voltage across capacitor
| Warning |  |  |  |  | V[C] eff rms | = | 446.2546 | V | effective P-P rms voltage across capacitor
[6 empty] | Q eff | = | 6.7669 | kVar | effective kVar of capacitor
| None |  |  |  |  | THD-V | = | 7.2101 | % | THD Voltage (reference to Vrms eff)
[6 empty] | THD-I | = | 9.8517 | % | THD Current (reference to Irms eff)
Power Factor Controller (6x6)
Power Quality Analyzer
Protection Relay
Note on F12: Input Phase-Phase Value Only Multiply VLN by √3 to get VLL
Note on F15: Input Phase-Phase Value Only Multiply VLN by √(3 ) to get VLL

## Computation (hidden)
| V1 pk | 338.8461 |  |  | C rated | 10000 | Var
| Vn pk | 24.4949 |  |  | V rated | 525 | Vac
| v1 | 314.1593 |  |  | F rated | 50 | Hz
| vn | 3455.7519 |  |  | L (reactor) | 7 | %
| Z1[LC] | -25.633125j
| Zn[LC] | 18.7174431818182j |  |  | C (Farad) | 0.00011549
| Z1[L] | 1.929375j |  |  | L (Henry) | 0.0061414
| Zn[L] | 21.223125j
| Z1[C] | -27.5625j
| Zn[C] | -2.50568181818182j
[12 empty] | Voltage across Reactor |  |  | Voltage @ Capacitor
|  | 416.0829 | 9.393 | 415 |  | 30 |  | 9.3473 |  | 0.92537 |  | 18.0344 | 19.6392 | 26.6634 | 446.2366 | 4.0161 | 446.2546 | 8.7819e-14 | 2255.6429
Spl | 1.4062 | Vrms | Irms | V1 rms |  | Vn rms |  | I1 rms |  | In rms |  | V1L rms | VnL rms | VL rms | V1c rms | Vnc rms | Vc rms | P rms | Q rms |  | Vrms | Irms
| Angle_L1 | real | real | real | im | real | im | real | im | real | im | real | real | real | real | real | real | real | real |  | imag | complex | real | imag | abs | arg
0 | 0 | 314.3512 | 1.6033e-16 | 338.8461 | 0 | -24.4949 | 3.001e-15 | 0 | 13.2191 | 1.6033e-16 | 1.3087 | -25.5045 | -27.774 | -53.2785 | 364.3506 | 3.2791 | 367.6297 | 5.04e-14 | -5.2082e-31 | 0 | 3.001e-15 | -1.17074627993478E-16+12.2634748458167j | -1.1707e-16 | 12.2635 | 12.2635 | 90
1 | 1.4062 | 315.1364 | -0.67345 | 338.744 | 8.3157 | -23.6076 | -6.5331 | -0.32441 | 13.2151 | -0.34904 | 1.2613 | -25.4969 | -26.7679 | -52.2648 | 364.2409 | 3.1603 | 367.4012 | -212.2287 | 9.9999 | 1 | 1.7826 | -0.0695427292988502+12.2941089354287j | -0.069543 | 12.2941 | 12.2943 | 90.3241
2 | 2.8125 | 317.428 | -1.3214 | 338.4379 | 16.6264 | -21.01 | -12.5929 | -0.64863 | 13.2031 | -0.67279 | 1.1225 | -25.4738 | -23.8226 | -49.2964 | 363.9117 | 2.8126 | 366.7243 | -419.4551 | 38.6109 | 2 | 4.0335 | -0.157354796476089+12.3835057886138j | -0.15735 | 12.3835
3 | 4.2188 | 321.0377 | -1.9203 | 337.928 | 24.9271 | -16.8902 | -17.7404 | -0.97246 | 13.1833 | -0.9478 | 0.90238 | -25.4354 | -19.1513 | -44.5867 | 363.3634 | 2.2611 | 365.6245 | -616.4738 | 81.9323 | 3 | 7.1867 | -0.280367925220724+12.5243308427429j | -0.28037 | 12.5243
4 | 5.625 | 325.6676 | -2.4498 | 337.2144 | 33.2127 | -11.5468 | -21.6026 | -1.2957 | 13.1554 | -1.1541 | 0.6169 | -25.3817 | -13.0926 | -38.4743 | 362.5962 | 1.5458 | 364.1419 | -797.8325 | 134.2885 | 4 | 11.6102 | -0.452935526596703+12.704952278435j | -0.45294 | 12.705
5 | 7.0312 | 330.9309 | -2.895 | 336.2978 | 41.4784 | -5.3669 | -23.8997 | -1.6182 | 13.1197 | -1.2769 | 0.28673 | -25.3127 | -6.0853 | -31.3981 | 361.6105 | 0.71846 | 362.329 | -958.0531 | 189.2712 | 5 | 17.5787 | -0.685778810769783+12.9102845810603j | -0.68578 | 12.9103
6 | 8.4375 | 336.3805 | -3.2467 | 335.1786 | 49.719 | 1.2019 | -24.4654 | -1.9396 | 13.076 | -1.3071 | -0.064213 | -25.2285 | 1.3628 | -23.8657 | 360.4071 | -0.1609 | 360.2462 | -1092.137 | 240.8569 | 6 | 25.2537 | -0.985196069297552+13.1228826587699j | -0.9852 | 13.1229
7 | 9.8438 | 341.5411 | -3.5026 | 333.8575 | 57.9298 | 7.6836 | -23.2586 | -2.26 | 13.0245 | -1.2426 | -0.4105 | -25.1291 | 8.7122 | -16.4169 | 358.9865 | -1.0286 | 357.9579 | -1196.2726 | 284.3682 | 7 | 34.6712 | -1.35259242222151+13.3242072498075j | -1.3526 | 13.3242
8 | 11.25 | 345.9439 | -3.667 | 332.3352 | 66.1056 | 13.6086 | -20.3668 | -2.5789 | 12.9651 | -1.0881 | -0.72706 | -25.0145 | 15.4304 | -9.5841 | 357.3497 | -1.8218 | 355.528 | -1268.5864 | 317.0967 | 8 | 45.7388 | -1.78436410718814+13.4959699421067j | -1.7844 | 13.496
9 | 12.6562 | 349.1606 | -3.7511 | 330.6128 | 74.2416 | 18.5478 | -15.9994 | -2.8963 | 12.8979 | -0.85479 | -0.99093 | -24.8848 | 21.0307 | -3.8541 | 355.4977 | -2.483 | 353.0147 | -1309.7364 | 338.503 | 9 | 58.2422 | -2.27214570198609+13.6214603602359j | -2.2721 | 13.6215
10 | 14.0625 | 350.8344 | -3.7715 | 328.6913 | 82.3329 | 22.1431 | -10.4729 | -3.212 | 12.8229 | -0.55953 | -1.183 | -24.7402 | 25.1074 | 0.36719 | 353.4315 | -2.9643 | 350.4672 | -1323.1717 | 350.017 | 10 | 71.86 | -2.80340237810368+13.6867593664786j | -2.8034 | 13.6868
11 | 15.4688 | 350.706 | -3.7494 | 326.5717 | 90.3746 | 24.1343 | -4.1877 | -3.5257 | 12.7402 | -0.22373 | -1.2894 | -24.5807 | 27.3651 | 2.7844 | 351.1524 | -3.2308 | 347.9216 | -1314.9466 | 354.5543 | 11 | 86.1869 | -3.36232428611389+13.681750380672j | -3.3623 | 13.6818
12 | 16.875 | 348.6324 | -3.709 | 324.2555 | 98.3618 | 24.3769 | 2.4009 | -3.8373 | 12.6499 | 0.12827 | -1.3024 | -24.4063 | 27.6403 | 3.2339 | 348.6618 | -3.2633 | 345.3985 | -1293.0853 | 355.9211 | 12 | 100.7627 | -3.93095828484596+13.6008555490838j | -3.931 | 13.6009
13 | 18.2812 | 344.5975 | -3.6756 | 321.7439 | 106.2898 | 22.8536 | 8.8156 | -4.1466 | 12.5519 | 0.47098 | -1.221 | -24.2173 | 25.9129 | 1.6957 | 345.9612 | -3.0594 | 342.9018 | -1266.6018 | 358.2761 | 13 | 115.1054 | -4.49049503120665+13.4434434265073j | -4.4905 | 13.4434
14 | 19.6875 | 338.713 | -3.6738 | 319.0385 | 114.1538 | 19.6745 | 14.5916 | -4.4534 | 12.4463 | 0.77957 | -1.0511 | -24.0137 | 22.3083 | -1.7054 | 343.0522 | -2.6338 | 340.4184 | -1244.3634 | 365.7715 | 14 | 128.7454 | -5.02261819191491+13.2138786337207j | -5.0226 | 13.2139
15 | 21.0938 | 331.211 | -3.7258 | 316.141 | 121.949 | 15.07 | 19.3105 | -4.7575 | 12.3333 | 1.0317 | -0.80513 | -23.7956 | 17.0874 | -6.7081 | 339.9365 | -2.0174 | 337.9191 | -1234.0242 | 382.4102 | 15 | 141.2595 | -5.51081803775923+12.9212098903788j | -5.5108 | 12.9212
16 | 22.5 | 322.4268 | -3.8497 | 313.053 | 129.6708 | 9.3738 | 22.6303 | -5.0587 | 12.2128 | 1.2091 | -0.50081 | -23.5631 | 10.6286 | -12.9345 | 336.6161 | -1.2549 | 335.3612 | -1241.2362 | 412.0703 | 16 | 152.3011 | -5.94157426133595+12.5785190221329j | -5.9416 | 12.5785
17 | 23.9062 | 312.7748 | -4.0581 | 309.7764 | 137.3144 | 2.9984 | 24.3107 | -5.3569 | 12.085 | 1.2988 | -0.16019 | -23.3165 | 3.3998 | -19.9167 | 333.0929 | -0.4014 | 332.6915 | -1269.2679 | 458.5792 | 17 | 161.6251 | -6.30532233364239+12.2019781022758j | -6.3053 | 12.202
18 | 25.3125 | 302.7191 | -4.3574 | 306.3132 | 144.8754 | -3.5941 | 24.2298 | -5.6519 | 11.9499 | 1.2945 | 0.19202 | -23.0558 | -4.0753 | -27.1311 | 329.3691 | 0.48114 | 329.8502 | -1319.0616 | 525.6985 | 18 | 169.1051 | -6.59713339697727+11.8096830330427j | -6.5971 | 11.8097
19 | 26.7188 | 292.7392 | -4.747 | 302.6656 | 152.349 | -9.9263 | 22.3935 | -5.9434 | 11.8076 | 1.1964 | 0.53033 | -22.7813 | -11.2552 | -34.0365 | 325.4468 | 1.3288 | 326.7757 | -1389.647 | 616.9053 | 19 | 174.7425 | -6.81705844520959+11.4203480679754j | -6.8171 | 11.4203
20 | 28.125 | 283.2962 | -5.2198 | 298.8356 | 159.7309 | -15.5394 | 18.9348 | -6.2314 | 11.6582 | 1.0116 | 0.83021 | -22.493 | -17.6196 | -40.1126 | 321.3286 | 2.0802 | 323.4088 | -1478.7531 | 734.9295 | 20 | 178.6657 | -6.97011186406304+11.0519558510903j | -6.9701 | 11.052
21 | 29.5312 | 274.7989 | -5.7621 | 294.8256 | 167.0166 | -20.0267 | 14.1044 | -6.5157 | 11.5017 | 0.75354 | 1.0699 | -22.1912 | -22.7076 | -44.8988 | 317.0167 | 2.6809 | 319.6977 | -1583.4229 | 881.098 | 21 | 181.121 | -7.06589553157611+10.7204607711128j | -7.0659 | 10.7205
22 | 30.9375 | 267.575 | -6.3551 | 290.638 | 174.2017 | -23.063 | 8.2521 | -6.796 | 11.3384 | 0.44088 | 1.2322 | -21.876 | -26.1504 | -48.0264 | 312.514 | 3.0874 | 315.6014 | -1700.4612 | 1054.6237 | 22 | 182.4538 | -7.11789071945929+10.4386395662893j | -7.1179 | 10.4386
23 | 32.3438 | 261.8468 | -6.9759 | 286.2753 | 181.2818 | -24.4285 | 1.802 | -7.0722 | 11.1682 | 0.096272 | 1.3051 | -21.5476 | -27.6987 | -49.2464 | 307.8229 | 3.2702 | 311.0931 | -1826.6169 | 1252.0337 | 23 | 183.0838 | -7.14246910309399+10.2151724471152j | -7.1425 | 10.2152
24 | 33.75 | 257.716 | -7.5994 | 281.7402 | 188.2528 | -24.0242 | -4.7787 | -7.3441 | 10.9913 | -0.25531 | 1.2835 | -21.2063 | -27.2403 | -48.4466 | 302.9465 | 3.2161 | 306.1626 | -1958.4946 | 1466.9295 | 24 | 183.4741 | -7.15769453779935+10.0540213035977j | -7.1577 | 10.054
25 | 35.1562 | 255.156 | -8.2 | 277.0354 | 195.1103 | -21.8794 | -11.0132 | -7.6116 | 10.8077 | -0.58839 | 1.1689 | -20.8521 | -24.8084 | -45.6605 | 297.8875 | 2.929 | 300.8165 | -2092.2893 | 1690.2213 | 25 | 184.0972 | -7.18200241743061+9.95415004035598j | -7.182 | 9.9542
26 | 36.5625 | 254.0142 | -8.7534 | 272.1637 | 201.8504 | -18.1495 | -16.4498 | -7.8746 | 10.6177 | -0.87885 | 0.96966 | -20.4854 | -20.5792 | -41.0646 | 292.6492 | 2.4297 | 295.0788 | -2223.4976 | 1910.8767 | 26 | 185.4006 | -7.23285230016258+9.90960729624546j | -7.2329 | 9.9096
27 | 37.9688 | 254.0234 | -9.2384 | 267.1281 | 208.4688 | -13.1047 | -20.6946 | -8.1328 | 10.4212 | -1.1056 | 0.70013 | -20.1064 | -14.859 | -34.9654 | 287.2345 | 1.7543 | 288.9888 | -2346.7751 | 2117.1082 | 27 | 187.7742 | -7.32545142293852+9.90996555103492j | -7.3255 | 9.91
28 | 39.375 | 254.8211 | -9.6384 | 261.9316 | 214.9617 | -7.1105 | -23.4402 | -8.3861 | 10.2185 | -1.2523 | 0.37989 | -19.7153 | -8.0624 | -27.7776 | 281.6468 | 0.95187 | 282.5987 | -2456.0688 | 2297.8135 | 28 | 191.5215 | -7.47164159021512+9.94108480200865j | -7.4716 | 9.9411
29 | 40.7812 | 255.9761 | -9.9426 | 256.5773 | 221.3251 | -0.60113 | -24.4875 | -8.6343 | 10.0096 | -1.3083 | 0.032116 | -19.3123 | -0.68161 | -19.9939 | 275.8895 | 0.080473 | 275.97 | -2545.0708 | 2444.0187 | 29 | 196.8375 | -7.67903008639606+9.98614547879741j | -7.679 | 9.9861
30 | 42.1875 | 257.0202 | -10.1468 | 251.0684 | 227.5551 | 5.9518 | -23.7608 | -8.8774 | 9.7947 | -1.2694 | -0.31798 | -18.8976 | 6.7485 | -12.1491 | 269.966 | -0.79676 | 269.1692 | -2607.9406 | 2550.0608 | 30 | 203.7943 | -7.95042758222663+10.0268757588386j | -7.9504 | 10.0269
31 | 43.5938 | 257.4818 | -10.2537 | 245.4083 | 233.6481 | 12.0735 | -21.3127 | -9.1151 | 9.5739 | -1.1387 | -0.64504 | -18.4716 | 13.6898 | -4.7818 | 263.8799 | -1.6163 | 262.2636 | -2640.1509 | 2614.3015 | 31 | 212.3354 | -8.28363376423581+10.044884361793j | -8.2836 | 10.0449
32 | 45 | 256.9209 | -10.2727 | 239.6004 | 239.6004 | 17.3205 | -17.3205 | -9.3473 | 9.3473 | -0.92537 | -0.92537 | -18.0344 | 19.6392 | 1.6047 | 257.6348 | -2.3187 | 255.3161 | -2639.2611 | 2639.2611 | 32 | 222.2799 | -8.67158622438762+10.0230022593571j | -8.6716 | 10.023
33 | 46.4062 | 254.9608 | -10.2189 | 233.6481 | 245.4083 | 21.3127 | -12.0735 | -9.5739 | 9.1151 | -0.64504 | -1.1387 | -17.5864 | 24.1658 | 6.5794 | 251.2345 | -2.8531 | 248.3814 | -2605.4222 | 2631.1838 | 33 | 233.3348 | -9.10286182953971+9.94653609085408j | -9.1029 | 9.9465
34 | 47.8125 | 251.3159 | -10.1127 | 227.5551 | 251.0684 | 23.7608 | -5.9518 | -9.7947 | 8.8774 | -0.31798 | -1.2694 | -17.1278 | 26.9416 | 9.8138 | 244.6829 | -3.1808 | 241.5021 | -2541.4739 | 2599.1588 | 34 | 245.1166 | -9.56249425375669+9.80434247155764j | -9.5625 | 9.8043
35 | 49.2188 | 245.8126 | -9.9775 | 221.3251 | 256.5773 | 24.4875 | 0.60113 | -10.0096 | 8.6343 | 0.032116 | -1.3083 | -16.6589 | 27.7656 | 11.1068 | 237.9839 | -3.2781 | 234.7058 | -2452.5902 | 2553.9967 | 35 | 257.1784 | -10.0330484510586+9.58964535649586j | -10.033 | 9.5896
36 | 50.625 | 238.4018 | -9.8386 | 214.9617 | 261.9316 | 23.4402 | 7.1105 | -10.2185 | 8.3861 | 0.37989 | -1.2523 | -16.1799 | 26.5781 | 10.3981 | 231.1416 | -3.1379 | 228.0037 | -2345.5387 | 2507.0809 | 36 | 269.0421 | -10.4958742312507+9.30053723741499j | -10.4959 | 9.3005
37 | 52.0312 | 229.1634 | -9.7211 | 208.4688 | 267.1281 | 20.6946 | 13.1047 | -10.4212 | 8.1328 | 0.70013 | -1.1056 | -15.6912 | 23.465 | 7.7738 | 224.16 | -2.7704 | 221.3897 | -2227.7143 | 2469.3799 | 37 | 280.2328 | -10.9324481256932+8.94012785605618j | -10.9324 | 8.9401
38 | 53.4375 | 218.3001 | -9.648 | 201.8504 | 272.1637 | 16.4498 | 18.1495 | -10.6177 | 7.8746 | 0.96966 | -0.87885 | -15.193 | 18.6519 | 3.4588 | 217.0434 | -2.2021 | 214.8413 | -2106.1595 | 2450.7287 | 38 | 290.3132 | -11.3257063333006+8.51632965344822j | -11.3257 | 8.5163
39 | 54.8438 | 206.1235 | -9.6388 | 195.1103 | 277.0354 | 11.0132 | 21.8794 | -10.8077 | 7.6116 | 1.1689 | -0.58839 | -14.6857 | 12.4875 | -2.1982 | 209.7961 | -1.4743 | 208.3218 | -1986.779 | 2459.3918 | 39 | 298.9148 | -11.661272183117+8.04129549248728j | -11.6613 | 8.0413
40 | 56.25 | 193.0315 | -9.7077 | 188.2528 | 281.7402 | 4.7787 | 24.0242 | -10.9913 | 7.3441 | 1.2835 | -0.25531 | -14.1696 | 5.4184 | -8.7511 | 202.4224 | -0.63972 | 201.7826 | -1873.8986 | 2501.8382 | 40 | 305.7645 | -11.9284891917076+7.53054938300047j | -11.9285 | 7.5305
41 | 57.6562 | 179.4799 | -9.8631 | 181.2818 | 286.2753 | -1.802 | 24.4285 | -11.1682 | 7.0722 | 1.3051 | 0.096272 | -13.6449 | -2.0432 | -15.6881 | 194.9267 | 0.24123 | 195.1679 | -1770.2205 | 2582.61 | 41 | 310.7038 | -12.1211848776791+7.00187317967872j | -12.1212 | 7.0019
42 | 59.0625 | 165.9496 | -10.1062 | 174.2017 | 290.638 | -8.2521 | 23.063 | -11.3384 | 6.796 | 1.2322 | 0.44088 | -13.112 | -9.3568 | -22.4687 | 187.3137 | 1.1047 | 188.4184 | -1677.1212 | 2704.1679 | 42 | 313.701 | -12.2381100015517+6.47402990238611j | -12.2381 | 6.474
43 | 60.4688 | 152.9123 | -10.4318 | 167.0166 | 294.8256 | -14.1044 | 20.0267 | -11.5017 | 6.5157 | 1.0699 | 0.75354 | -12.5711 | -15.9925 | -28.5636 | 179.5878 | 1.8881 | 181.4759 | -1595.1493 | 2866.6459 | 43 | 314.8522 | -12.2830214137735+5.96541616459409j | -12.283 | 5.9654
44 | 61.875 | 140.7961 | -10.828 | 159.7309 | 298.8356 | -18.9348 | 15.5394 | -11.6582 | 6.2314 | 0.83021 | 1.0116 | -12.0228 | -21.4696 | -33.4924 | 171.7537 | 2.5348 | 174.2885 | -1524.5362 | 3067.5223 | 44 | 314.375 | -12.2644025133287+5.49274133153827j | -12.2644 | 5.4927
45 | 63.2812 | 129.9556 | -11.2773 | 152.349 | 302.6656 | -22.3935 | 9.9263 | -11.8076 | 5.9434 | 0.53033 | 1.1964 | -11.4671 | -25.3913 | -36.8584 | 163.8162 | 2.9978 | 166.814 | -1465.5438 | 3301.2988 | 45 | 312.5919 | -12.1948415735524+5.06982909307394j | -12.1948 | 5.0698
46 | 64.6875 | 120.6456 | -11.7579 | 144.8754 | 306.3132 | -24.2298 | 3.5941 | -11.9499 | 5.6519 | 0.19202 | 1.2945 | -10.9046 | -27.4734 | -38.378 | 155.78 | 3.2436 | 159.0236 | -1418.536 | 3559.3336 | 46 | 309.9074 | -12.0901129783827+4.7066282674148j | -12.0901 | 4.7066
47 | 66.0938 | 113.0037 | -12.2452 | 137.3144 | 309.7764 | -24.3107 | -2.9984 | -12.085 | 5.3569 | -0.16019 | 1.2988 | -10.3355 | -27.5651 | -37.9006 | 147.6499 | 3.2544 | 150.9044 | -1383.7532 | 3829.9897 | 47 | 306.778 | -11.9680279356008+4.40850449350643j | -11.968 | 4.4085
48 | 67.5 | 107.0404 | -12.7136 | 129.6708 | 313.053 | -22.6303 | -9.3738 | -12.2128 | 5.0587 | -0.50081 | 1.2091 | -9.7602 | -25.6598 | -35.42 | 139.4309 | 3.0295 | 142.4604 | -1360.873 | 4099.2156 | 48 | 303.6792 | -11.8471379343324+4.17586411990473j | -11.8471 | 4.1759
49 | 68.9062 | 102.6386 | -13.1384 | 121.949 | 316.141 | -19.3105 | -15.07 | -12.3333 | 4.7575 | -0.80513 | 1.0317 | -9.179 | -21.8955 | -31.0745 | 131.128 | 2.5851 | 133.7131 | -1348.5096 | 4351.5926 | 49 | 301.0709 | -11.7453848822588+4.00413753100783j | -11.7454 | 4.0041
50 | 70.3125 | 99.5622 | -13.4975 | 114.1538 | 319.0385 | -14.5916 | -19.6745 | -12.4463 | 4.4534 | -1.0511 | 0.77957 | -8.5922 | -16.545 | -25.1372 | 122.746 | 1.9534 | 124.6994 | -1343.8378 | 4571.768 | 50 | 299.364 | -11.6787957207415+3.884123110931j | -11.6788 | 3.8841
51 | 71.7188 | 97.4742 | -13.7729 | 106.2898 | 321.7439 | -8.8156 | -22.8536 | -12.5519 | 4.1466 | -1.221 | 0.47098 | -8.0003 | -9.9957 | -17.996 | 114.2901 | 1.1801 | 115.4703 | -1342.4987 | 4746.0914 | 51 | 298.8903 | -11.6603160935455+3.80266691780181j | -11.6603 | 3.8027
52 | 73.125 | 95.9609 | -13.9522 | 98.3618 | 324.2555 | -2.4009 | -24.3769 | -12.6499 | 3.8373 | -1.3024 | 0.12827 | -7.4036 | -2.7223 | -10.1259 | 105.7654 | 0.32141 | 106.0868 | -1338.8683 | 4864.1987 | 52 | 299.8785 | -11.6988675705147+3.74362881966824j | -11.6989 | 3.7436
53 | 74.5312 | 94.5623 | -14.0296 | 90.3746 | 326.5717 | 4.1877 | -24.1343 | -12.7402 | 3.5257 | -1.2894 | -0.22373 | -6.8024 | 4.7483 | -2.0541 | 97.177 | -0.5606 | 96.6164 | -1326.673 | 4920.2735 | 53 | 302.4375 | -11.7986967312825+3.68906508960562j | -11.7987 | 3.6891
54 | 75.9375 | 92.8058 | -14.0059 | 82.3329 | 328.6913 | 10.4729 | -22.1431 | -12.8229 | 3.212 | -1.183 | -0.55953 | -6.1971 | 11.8749 | 5.6778 | 88.53 | -1.402 | 87.128 | -1299.8317 | 4913.763 | 54 | 306.5482 | -11.9590632692671+3.62054177552962j | -11.9591 | 3.6205
55 | 77.3438 | 90.241 | -13.8888 | 74.2416 | 330.6128 | 15.9994 | -18.5478 | -12.8979 | 2.8963 | -0.99093 | -0.85479 | -5.5881 | 18.1412 | 12.5531 | 79.8297 | -2.1418 | 77.6879 | -1253.34 | 4849.4249 | 55 | 312.0651 | -12.1742897147041+3.5204836858096j | -12.1743 | 3.5205
56 | 78.75 | 86.4724 | -13.6921 | 66.1056 | 332.3352 | 20.3668 | -13.6086 | -12.9651 | 2.5789 | -0.72706 | -1.0881 | -4.9757 | 23.0932 | 18.1175 | 71.0813 | -2.7265 | 68.3548 | -1183.9904 | 4736.7072 | 56 | 318.7266 | -12.4341691767477+3.37346125142709j | -12.4342 | 3.3735
57 | 80.1562 | 81.1884 | -13.435 | 57.9298 | 333.8575 | 23.2586 | -7.6836 | -13.0245 | 2.26 | -0.4105 | -1.2426 | -4.3603 | 26.3722 | 22.0119 | 62.2901 | -3.1136 | 59.1765 | -1090.7623 | 4588.5904 | 57 | 326.1739 | -12.7247015667466+3.16732202608075j | -12.7247 | 3.1673
58 | 81.5625 | 74.1844 | -13.1402 | 49.719 | 335.1786 | 24.4654 | -1.2019 | -13.076 | 1.9396 | -0.064213 | -1.3071 | -3.7423 | 27.7405 | 23.9983 | 53.4613 | -3.2752 | 50.1862 | -974.7989 | 4420.1093 | 58 | 333.9767 | -13.0291049668442+2.89408484123856j | -13.0291 | 2.8941
59 | 82.9688 | 65.3781 | -12.8329 | 41.4784 | 336.2978 | 23.8997 | 5.3669 | -13.1197 | 1.6182 | 0.28673 | -1.2769 | -3.122 | 27.0992 | 23.9771 | 44.6004 | -3.1994 | 41.401 | -838.9923 | 4246.8123 | 59 | 341.6647 | -13.3290288741539+2.55053182823533j | -13.329 | 2.5505
60 | 84.375 | 54.8153 | -12.5385 | 33.2127 | 337.2144 | 21.6026 | 11.5468 | -13.1554 | 1.2957 | 0.6169 | -1.1541 | -2.4999 | 24.4945 | 21.9946 | 35.7126 | -2.8919 | 32.8207 | -687.3024 | 4083.3886 | 60 | 348.7613 | -13.605881425105+2.13845540836193j | -13.6059 | 2.1385
61 | 85.7812 | 42.6674 | -12.2809 | 24.9271 | 337.928 | 17.7404 | 16.8902 | -13.1833 | 0.97246 | 0.90238 | -0.9478 | -1.8762 | 20.1152 | 18.239 | 26.8033 | -2.3749 | 24.4284 | -523.9932 | 3942.6239 | 61 | 354.8182 | -13.8421744467253+1.66454234869056j | -13.8422 | 1.6645
62 | 87.1875 | 29.2193 | -12.0807 | 16.6264 | 338.4379 | 12.5929 | 21.01 | -13.2031 | 0.64863 | 1.1225 | -0.67279 | -1.2514 | 14.2787 | 13.0272 | 17.8778 | -1.6858 | 16.192 | -352.9884 | 3834.7412 | 62 | 359.4479 | -14.0227888899035+1.13990327516371j | -14.0228 | 1.1399
63 | 88.5938 | 14.8488 | -11.9538 | 8.3157 | 338.744 | 6.5331 | 23.6076 | -13.2151 | 0.32441 | 1.2613 | -0.34904 | -0.62591 | 7.4077 | 6.7818 | 8.9416 | -0.87458 | 8.067 | -177.5 | 3767.0864 | 63 | 362.3516 | -14.1360689676182+0.579281720314722j | -14.1361 | 0.57928
64 | 90 | -3.2484e-15 | -11.9104 | 2.0757e-14 | 338.8461 | -2.4005e-14 | 24.4949 | -13.2191 | 8.0977e-16 | 1.3087 | 1.2825e-15 | -1.5623e-15 | -2.7219e-14 | -2.8781e-14 | 2.2319e-14 | 3.2136e-15 | 2.5533e-14 | 3.869e-14 | 3744.0494 | 64 | 363.341 | -14.174665730879-1.26727241127454E-16j | -14.1747 | -1.2673e-16
65 | 91.4062 | -14.8488 | -11.9538 | -8.3157 | 338.744 | -6.5331 | 23.6076 | -13.2151 | -0.32441 | 1.2613 | 0.34904 | 0.62591 | -7.4077 | -6.7818 | -8.9416 | 0.87458 | -8.067 | 177.5 | 3767.0864 | 65 | 362.3516 | -14.1360689676182-0.579281720314718j | -14.1361 | -0.57928
66 | 92.8125 | -29.2193 | -12.0807 | -16.6264 | 338.4379 | -12.5929 | 21.01 | -13.2031 | -0.64863 | 1.1225 | 0.67279 | 1.2514 | -14.2787 | -13.0272 | -17.8778 | 1.6858 | -16.192 | 352.9884 | 3834.7412 | 66 | 359.4479 | -14.0227888899035-1.13990327516371j | -14.0228 | -1.1399
67 | 94.2188 | -42.6674 | -12.2809 | -24.9271 | 337.928 | -17.7404 | 16.8902 | -13.1833 | -0.97246 | 0.90238 | 0.9478 | 1.8762 | -20.1152 | -18.239 | -26.8033 | 2.3749 | -24.4284 | 523.9932 | 3942.6239 | 67 | 354.8182 | -13.8421744467253-1.66454234869056j | -13.8422 | -1.6645
68 | 95.625 | -54.8153 | -12.5385 | -33.2127 | 337.2144 | -21.6026 | 11.5468 | -13.1554 | -1.2957 | 0.6169 | 1.1541 | 2.4999 | -24.4945 | -21.9946 | -35.7126 | 2.8919 | -32.8207 | 687.3024 | 4083.3886 | 68 | 348.7613 | -13.605881425105-2.13845540836193j | -13.6059 | -2.1385
69 | 97.0312 | -65.3781 | -12.8329 | -41.4784 | 336.2978 | -23.8997 | 5.3669 | -13.1197 | -1.6182 | 0.28673 | 1.2769 | 3.122 | -27.0992 | -23.9771 | -44.6004 | 3.1994 | -41.401 | 838.9923 | 4246.8123 | 69 | 341.6647 | -13.3290288741539-2.55053182823533j | -13.329 | -2.5505
70 | 98.4375 | -74.1844 | -13.1402 | -49.719 | 335.1786 | -24.4654 | -1.2019 | -13.076 | -1.9396 | -0.064213 | 1.3071 | 3.7423 | -27.7405 | -23.9983 | -53.4613 | 3.2752 | -50.1862 | 974.7989 | 4420.1093 | 70 | 333.9767 | -13.0291049668442-2.89408484123856j | -13.0291 | -2.8941
71 | 99.8438 | -81.1884 | -13.435 | -57.9298 | 333.8575 | -23.2586 | -7.6836 | -13.0245 | -2.26 | -0.4105 | 1.2426 | 4.3603 | -26.3722 | -22.0119 | -62.2901 | 3.1136 | -59.1765 | 1090.7623 | 4588.5904 | 71 | 326.1739 | -12.7247015667466-3.16732202608075j | -12.7247 | -3.1673
72 | 101.25 | -86.4724 | -13.6921 | -66.1056 | 332.3352 | -20.3668 | -13.6086 | -12.9651 | -2.5789 | -0.72706 | 1.0881 | 4.9757 | -23.0932 | -18.1175 | -71.0813 | 2.7265 | -68.3548 | 1183.9904 | 4736.7072 | 72 | 318.7266 | -12.4341691767477-3.37346125142708j | -12.4342 | -3.3735
73 | 102.6562 | -90.241 | -13.8888 | -74.2416 | 330.6128 | -15.9994 | -18.5478 | -12.8979 | -2.8963 | -0.99093 | 0.85479 | 5.5881 | -18.1412 | -12.5531 | -79.8297 | 2.1418 | -77.6879 | 1253.34 | 4849.4249 | 73 | 312.0651 | -12.1742897147041-3.5204836858096j | -12.1743 | -3.5205
74 | 104.0625 | -92.8058 | -14.0059 | -82.3329 | 328.6913 | -10.4729 | -22.1431 | -12.8229 | -3.212 | -1.183 | 0.55953 | 6.1971 | -11.8749 | -5.6778 | -88.53 | 1.402 | -87.128 | 1299.8317 | 4913.763 | 74 | 306.5482 | -11.9590632692671-3.62054177552962j | -11.9591 | -3.6205
75 | 105.4688 | -94.5623 | -14.0296 | -90.3746 | 326.5717 | -4.1877 | -24.1343 | -12.7402 | -3.5257 | -1.2894 | 0.22373 | 6.8024 | -4.7483 | 2.0541 | -97.177 | 0.5606 | -96.6164 | 1326.673 | 4920.2735 | 75 | 302.4375 | -11.7986967312825-3.68906508960562j | -11.7987 | -3.6891
76 | 106.875 | -95.9609 | -13.9522 | -98.3618 | 324.2555 | 2.4009 | -24.3769 | -12.6499 | -3.8373 | -1.3024 | -0.12827 | 7.4036 | 2.7223 | 10.1259 | -105.7654 | -0.32141 | -106.0868 | 1338.8683 | 4864.1987 | 76 | 299.8785 | -11.6988675705147-3.74362881966825j | -11.6989 | -3.7436
77 | 108.2812 | -97.4742 | -13.7729 | -106.2898 | 321.7439 | 8.8156 | -22.8536 | -12.5519 | -4.1466 | -1.221 | -0.47098 | 8.0003 | 9.9957 | 17.996 | -114.2901 | -1.1801 | -115.4703 | 1342.4987 | 4746.0914 | 77 | 298.8903 | -11.6603160935455-3.80266691780181j | -11.6603 | -3.8027
78 | 109.6875 | -99.5622 | -13.4975 | -114.1538 | 319.0385 | 14.5916 | -19.6745 | -12.4463 | -4.4534 | -1.0511 | -0.77957 | 8.5922 | 16.545 | 25.1372 | -122.746 | -1.9534 | -124.6994 | 1343.8378 | 4571.768 | 78 | 299.364 | -11.6787957207415-3.884123110931j | -11.6788 | -3.8841
79 | 111.0938 | -102.6386 | -13.1384 | -121.949 | 316.141 | 19.3105 | -15.07 | -12.3333 | -4.7575 | -0.80513 | -1.0317 | 9.179 | 21.8955 | 31.0745 | -131.128 | -2.5851 | -133.7131 | 1348.5096 | 4351.5926 | 79 | 301.0709 | -11.7453848822588-4.00413753100783j | -11.7454 | -4.0041
80 | 112.5 | -107.0404 | -12.7136 | -129.6708 | 313.053 | 22.6303 | -9.3738 | -12.2128 | -5.0587 | -0.50081 | -1.2091 | 9.7602 | 25.6598 | 35.42 | -139.4309 | -3.0295 | -142.4604 | 1360.873 | 4099.2156 | 80 | 303.6792 | -11.8471379343324-4.17586411990473j | -11.8471 | -4.1759
81 | 113.9062 | -113.0037 | -12.2452 | -137.3144 | 309.7764 | 24.3107 | -2.9984 | -12.085 | -5.3569 | -0.16019 | -1.2988 | 10.3355 | 27.5651 | 37.9006 | -147.6499 | -3.2544 | -150.9044 | 1383.7532 | 3829.9897 | 81 | 306.778 | -11.9680279356008-4.40850449350643j | -11.968 | -4.4085
82 | 115.3125 | -120.6456 | -11.7579 | -144.8754 | 306.3132 | 24.2298 | 3.5941 | -11.9499 | -5.6519 | 0.19202 | -1.2945 | 10.9046 | 27.4734 | 38.378 | -155.78 | -3.2436 | -159.0236 | 1418.536 | 3559.3336 | 82 | 309.9074 | -12.0901129783827-4.7066282674148j | -12.0901 | -4.7066
83 | 116.7188 | -129.9556 | -11.2773 | -152.349 | 302.6656 | 22.3935 | 9.9263 | -11.8076 | -5.9434 | 0.53033 | -1.1964 | 11.4671 | 25.3913 | 36.8584 | -163.8162 | -2.9978 | -166.814 | 1465.5438 | 3301.2988 | 83 | 312.5919 | -12.1948415735524-5.06982909307394j | -12.1948 | -5.0698
84 | 118.125 | -140.7961 | -10.828 | -159.7309 | 298.8356 | 18.9348 | 15.5394 | -11.6582 | -6.2314 | 0.83021 | -1.0116 | 12.0228 | 21.4696 | 33.4924 | -171.7537 | -2.5348 | -174.2885 | 1524.5362 | 3067.5223 | 84 | 314.375 | -12.2644025133287-5.49274133153827j | -12.2644 | -5.4927
85 | 119.5312 | -152.9123 | -10.4318 | -167.0166 | 294.8256 | 14.1044 | 20.0267 | -11.5017 | -6.5157 | 1.0699 | -0.75354 | 12.5711 | 15.9925 | 28.5636 | -179.5878 | -1.8881 | -181.4759 | 1595.1493 | 2866.6459 | 85 | 314.8522 | -12.2830214137735-5.96541616459409j | -12.283 | -5.9654
86 | 120.9375 | -165.9496 | -10.1062 | -174.2017 | 290.638 | 8.2521 | 23.063 | -11.3384 | -6.796 | 1.2322 | -0.44088 | 13.112 | 9.3568 | 22.4687 | -187.3137 | -1.1047 | -188.4184 | 1677.1212 | 2704.1679 | 86 | 313.701 | -12.2381100015517-6.47402990238611j | -12.2381 | -6.474
87 | 122.3438 | -179.4799 | -9.8631 | -181.2818 | 286.2753 | 1.802 | 24.4285 | -11.1682 | -7.0722 | 1.3051 | -0.096272 | 13.6449 | 2.0432 | 15.6881 | -194.9267 | -0.24123 | -195.1679 | 1770.2205 | 2582.61 | 87 | 310.7038 | -12.1211848776791-7.00187317967872j | -12.1212 | -7.0019
88 | 123.75 | -193.0315 | -9.7077 | -188.2528 | 281.7402 | -4.7787 | 24.0242 | -10.9913 | -7.3441 | 1.2835 | 0.25531 | 14.1696 | -5.4184 | 8.7511 | -202.4224 | 0.63972 | -201.7826 | 1873.8986 | 2501.8382 | 88 | 305.7645 | -11.9284891917076-7.53054938300047j | -11.9285 | -7.5305
89 | 125.1562 | -206.1235 | -9.6388 | -195.1103 | 277.0354 | -11.0132 | 21.8794 | -10.8077 | -7.6116 | 1.1689 | 0.58839 | 14.6857 | -12.4875 | 2.1982 | -209.7961 | 1.4743 | -208.3218 | 1986.779 | 2459.3918 | 89 | 298.9148 | -11.661272183117-8.04129549248728j | -11.6613 | -8.0413
90 | 126.5625 | -218.3001 | -9.648 | -201.8504 | 272.1637 | -16.4498 | 18.1495 | -10.6177 | -7.8746 | 0.96966 | 0.87885 | 15.193 | -18.6519 | -3.4588 | -217.0434 | 2.2021 | -214.8413 | 2106.1595 | 2450.7287 | 90 | 290.3132 | -11.3257063333006-8.51632965344822j | -11.3257 | -8.5163
91 | 127.9688 | -229.1634 | -9.7211 | -208.4688 | 267.1281 | -20.6946 | 13.1047 | -10.4212 | -8.1328 | 0.70013 | 1.1056 | 15.6912 | -23.465 | -7.7738 | -224.16 | 2.7704 | -221.3897 | 2227.7143 | 2469.3799 | 91 | 280.2328 | -10.9324481256932-8.94012785605618j | -10.9324 | -8.9401
92 | 129.375 | -238.4018 | -9.8386 | -214.9617 | 261.9316 | -23.4402 | 7.1105 | -10.2185 | -8.3861 | 0.37989 | 1.2523 | 16.1799 | -26.5781 | -10.3981 | -231.1416 | 3.1379 | -228.0037 | 2345.5387 | 2507.0809 | 92 | 269.0421 | -10.4958742312507-9.30053723741499j | -10.4959 | -9.3005
93 | 130.7812 | -245.8126 | -9.9775 | -221.3251 | 256.5773 | -24.4875 | 0.60113 | -10.0096 | -8.6343 | 0.032116 | 1.3083 | 16.6589 | -27.7656 | -11.1068 | -237.9839 | 3.2781 | -234.7058 | 2452.5902 | 2553.9967 | 93 | 257.1784 | -10.0330484510586-9.58964535649586j | -10.033 | -9.5896
94 | 132.1875 | -251.3159 | -10.1127 | -227.5551 | 251.0684 | -23.7608 | -5.9518 | -9.7947 | -8.8774 | -0.31798 | 1.2694 | 17.1278 | -26.9416 | -9.8138 | -244.6829 | 3.1808 | -241.5021 | 2541.4739 | 2599.1588 | 94 | 245.1166 | -9.56249425375669-9.80434247155764j | -9.5625 | -9.8043
95 | 133.5938 | -254.9608 | -10.2189 | -233.6481 | 245.4083 | -21.3127 | -12.0735 | -9.5739 | -9.1151 | -0.64504 | 1.1387 | 17.5864 | -24.1658 | -6.5794 | -251.2345 | 2.8531 | -248.3814 | 2605.4222 | 2631.1838 | 95 | 233.3348 | -9.10286182953971-9.94653609085408j | -9.1029 | -9.9465
96 | 135 | -256.9209 | -10.2727 | -239.6004 | 239.6004 | -17.3205 | -17.3205 | -9.3473 | -9.3473 | -0.92537 | 0.92537 | 18.0344 | -19.6392 | -1.6047 | -257.6348 | 2.3187 | -255.3161 | 2639.2611 | 2639.2611 | 96 | 222.2799 | -8.67158622438762-10.0230022593571j | -8.6716 | -10.023
97 | 136.4062 | -257.4818 | -10.2537 | -245.4083 | 233.6481 | -12.0735 | -21.3127 | -9.1151 | -9.5739 | -1.1387 | 0.64504 | 18.4716 | -13.6898 | 4.7818 | -263.8799 | 1.6163 | -262.2636 | 2640.1509 | 2614.3015 | 97 | 212.3354 | -8.28363376423581-10.044884361793j | -8.2836 | -10.0449
98 | 137.8125 | -257.0202 | -10.1468 | -251.0684 | 227.5551 | -5.9518 | -23.7608 | -8.8774 | -9.7947 | -1.2694 | 0.31798 | 18.8976 | -6.7485 | 12.1491 | -269.966 | 0.79676 | -269.1692 | 2607.9406 | 2550.0608 | 98 | 203.7943 | -7.95042758222663-10.0268757588386j | -7.9504 | -10.0269
99 | 139.2188 | -255.9761 | -9.9426 | -256.5773 | 221.3251 | 0.60113 | -24.4875 | -8.6343 | -10.0096 | -1.3083 | -0.032116 | 19.3123 | 0.68161 | 19.9939 | -275.8895 | -0.080473 | -275.97 | 2545.0708 | 2444.0187 | 99 | 196.8375 | -7.67903008639606-9.98614547879741j | -7.679 | -9.9861
100 | 140.625 | -254.8211 | -9.6384 | -261.9316 | 214.9617 | 7.1105 | -23.4402 | -8.3861 | -10.2185 | -1.2523 | -0.37989 | 19.7153 | 8.0624 | 27.7776 | -281.6468 | -0.95187 | -282.5987 | 2456.0688 | 2297.8135 | 100 | 191.5215 | -7.47164159021512-9.94108480200865j | -7.4716 | -9.9411
101 | 142.0312 | -254.0234 | -9.2384 | -267.1281 | 208.4688 | 13.1047 | -20.6946 | -8.1328 | -10.4212 | -1.1056 | -0.70013 | 20.1064 | 14.859 | 34.9654 | -287.2345 | -1.7543 | -288.9888 | 2346.7751 | 2117.1082 | 101 | 187.7742 | -7.32545142293852-9.90996555103488j | -7.3255 | -9.91
102 | 143.4375 | -254.0142 | -8.7534 | -272.1637 | 201.8504 | 18.1495 | -16.4498 | -7.8746 | -10.6177 | -0.87885 | -0.96966 | 20.4854 | 20.5792 | 41.0646 | -292.6492 | -2.4297 | -295.0788 | 2223.4976 | 1910.8767 | 102 | 185.4006 | -7.23285230016258-9.90960729624546j | -7.2329 | -9.9096
103 | 144.8438 | -255.156 | -8.2 | -277.0354 | 195.1103 | 21.8794 | -11.0132 | -7.6116 | -10.8077 | -0.58839 | -1.1689 | 20.8521 | 24.8084 | 45.6605 | -297.8875 | -2.929 | -300.8165 | 2092.2893 | 1690.2213 | 103 | 184.0972 | -7.18200241743061-9.95415004035598j | -7.182 | -9.9542
104 | 146.25 | -257.716 | -7.5994 | -281.7402 | 188.2528 | 24.0242 | -4.7787 | -7.3441 | -10.9913 | -0.25531 | -1.2835 | 21.2063 | 27.2403 | 48.4466 | -302.9465 | -3.2161 | -306.1626 | 1958.4946 | 1466.9295 | 104 | 183.4741 | -7.15769453779935-10.0540213035977j | -7.1577 | -10.054
105 | 147.6562 | -261.8468 | -6.9759 | -286.2753 | 181.2818 | 24.4285 | 1.802 | -7.0722 | -11.1682 | 0.096272 | -1.3051 | 21.5476 | 27.6987 | 49.2464 | -307.8229 | -3.2702 | -311.0931 | 1826.6169 | 1252.0337 | 105 | 183.0838 | -7.14246910309399-10.2151724471152j | -7.1425 | -10.2152
106 | 149.0625 | -267.575 | -6.3551 | -290.638 | 174.2017 | 23.063 | 8.2521 | -6.796 | -11.3384 | 0.44088 | -1.2322 | 21.876 | 26.1504 | 48.0264 | -312.514 | -3.0874 | -315.6014 | 1700.4612 | 1054.6237 | 106 | 182.4538 | -7.11789071945929-10.4386395662893j | -7.1179 | -10.4386
107 | 150.4688 | -274.7989 | -5.7621 | -294.8256 | 167.0166 | 20.0267 | 14.1044 | -6.5157 | -11.5017 | 0.75354 | -1.0699 | 22.1912 | 22.7076 | 44.8988 | -317.0167 | -2.6809 | -319.6977 | 1583.4229 | 881.098 | 107 | 181.121 | -7.06589553157611-10.7204607711128j | -7.0659 | -10.7205
108 | 151.875 | -283.2962 | -5.2198 | -298.8356 | 159.7309 | 15.5394 | 18.9348 | -6.2314 | -11.6582 | 1.0116 | -0.83021 | 22.493 | 17.6196 | 40.1126 | -321.3286 | -2.0802 | -323.4088 | 1478.7531 | 734.9295 | 108 | 178.6657 | -6.97011186406304-11.0519558510903j | -6.9701 | -11.052
109 | 153.2812 | -292.7392 | -4.747 | -302.6656 | 152.349 | 9.9263 | 22.3935 | -5.9434 | -11.8076 | 1.1964 | -0.53033 | 22.7813 | 11.2552 | 34.0365 | -325.4468 | -1.3288 | -326.7757 | 1389.647 | 616.9053 | 109 | 174.7425 | -6.81705844520963-11.4203480679754j | -6.8171 | -11.4203
110 | 154.6875 | -302.7191 | -4.3574 | -306.3132 | 144.8754 | 3.5941 | 24.2298 | -5.6519 | -11.9499 | 1.2945 | -0.19202 | 23.0558 | 4.0753 | 27.1311 | -329.3691 | -0.48114 | -329.8502 | 1319.0616 | 525.6985 | 110 | 169.1051 | -6.59713339697727-11.8096830330427j | -6.5971 | -11.8097
111 | 156.0938 | -312.7748 | -4.0581 | -309.7764 | 137.3144 | -2.9984 | 24.3107 | -5.3569 | -12.085 | 1.2988 | 0.16019 | 23.3165 | -3.3998 | 19.9167 | -333.0929 | 0.4014 | -332.6915 | 1269.2679 | 458.5792 | 111 | 161.6251 | -6.30532233364239-12.2019781022758j | -6.3053 | -12.202
112 | 157.5 | -322.4268 | -3.8497 | -313.053 | 129.6708 | -9.3738 | 22.6303 | -5.0587 | -12.2128 | 1.2091 | 0.50081 | 23.5631 | -10.6286 | 12.9345 | -336.6161 | 1.2549 | -335.3612 | 1241.2362 | 412.0703 | 112 | 152.3011 | -5.94157426133595-12.5785190221329j | -5.9416 | -12.5785
113 | 158.9062 | -331.211 | -3.7258 | -316.141 | 121.949 | -15.07 | 19.3105 | -4.7575 | -12.3333 | 1.0317 | 0.80513 | 23.7956 | -17.0874 | 6.7081 | -339.9365 | 2.0174 | -337.9191 | 1234.0242 | 382.4102 | 113 | 141.2595 | -5.51081803775923-12.9212098903788j | -5.5108 | -12.9212
114 | 160.3125 | -338.713 | -3.6738 | -319.0385 | 114.1538 | -19.6745 | 14.5916 | -4.4534 | -12.4463 | 0.77957 | 1.0511 | 24.0137 | -22.3083 | 1.7054 | -343.0522 | 2.6338 | -340.4184 | 1244.3634 | 365.7715 | 114 | 128.7454 | -5.02261819191491-13.2138786337207j | -5.0226 | -13.2139
115 | 161.7188 | -344.5975 | -3.6756 | -321.7439 | 106.2898 | -22.8536 | 8.8156 | -4.1466 | -12.5519 | 0.47098 | 1.221 | 24.2173 | -25.9129 | -1.6957 | -345.9612 | 3.0594 | -342.9018 | 1266.6018 | 358.2761 | 115 | 115.1054 | -4.49049503120665-13.4434434265073j | -4.4905 | -13.4434
116 | 163.125 | -348.6324 | -3.709 | -324.2555 | 98.3618 | -24.3769 | 2.4009 | -3.8373 | -12.6499 | 0.12827 | 1.3024 | 24.4063 | -27.6403 | -3.2339 | -348.6618 | 3.2633 | -345.3985 | 1293.0853 | 355.9211 | 116 | 100.7627 | -3.93095828484596-13.6008555490838j | -3.931 | -13.6009
117 | 164.5312 | -350.706 | -3.7494 | -326.5717 | 90.3746 | -24.1343 | -4.1877 | -3.5257 | -12.7402 | -0.22373 | 1.2894 | 24.5807 | -27.3651 | -2.7844 | -351.1524 | 3.2308 | -347.9216 | 1314.9466 | 354.5543 | 117 | 86.1869 | -3.3623242861139-13.681750380672j | -3.3623 | -13.6818
118 | 165.9375 | -350.8344 | -3.7715 | -328.6913 | 82.3329 | -22.1431 | -10.4729 | -3.212 | -12.8229 | -0.55953 | 1.183 | 24.7402 | -25.1074 | -0.36719 | -353.4315 | 2.9643 | -350.4672 | 1323.1717 | 350.017 | 118 | 71.86 | -2.80340237810369-13.6867593664786j | -2.8034 | -13.6868
119 | 167.3438 | -349.1606 | -3.7511 | -330.6128 | 74.2416 | -18.5478 | -15.9994 | -2.8963 | -12.8979 | -0.85479 | 0.99093 | 24.8848 | -21.0307 | 3.8541 | -355.4977 | 2.483 | -353.0147 | 1309.7364 | 338.503 | 119 | 58.2422 | -2.27214570198609-13.6214603602359j | -2.2721 | -13.6215
120 | 168.75 | -345.9439 | -3.667 | -332.3352 | 66.1056 | -13.6086 | -20.3668 | -2.5789 | -12.9651 | -1.0881 | 0.72706 | 25.0145 | -15.4304 | 9.5841 | -357.3497 | 1.8218 | -355.528 | 1268.5864 | 317.0967 | 120 | 45.7388 | -1.78436410718814-13.4959699421068j | -1.7844 | -13.496
121 | 170.1562 | -341.5411 | -3.5026 | -333.8575 | 57.9298 | -7.6836 | -23.2586 | -2.26 | -13.0245 | -1.2426 | 0.4105 | 25.1291 | -8.7122 | 16.4169 | -358.9865 | 1.0286 | -357.9579 | 1196.2726 | 284.3682 | 121 | 34.6712 | -1.3525924222215-13.3242072498075j | -1.3526 | -13.3242
122 | 171.5625 | -336.3805 | -3.2467 | -335.1786 | 49.719 | -1.2019 | -24.4654 | -1.9396 | -13.076 | -1.3071 | 0.064213 | 25.2285 | -1.3628 | 23.8657 | -360.4071 | 0.1609 | -360.2462 | 1092.137 | 240.8569 | 122 | 25.2537 | -0.985196069297559-13.1228826587699j | -0.9852 | -13.1229
123 | 172.9688 | -330.9309 | -2.895 | -336.2978 | 41.4784 | 5.3669 | -23.8997 | -1.6182 | -13.1197 | -1.2769 | -0.28673 | 25.3127 | 6.0853 | 31.3981 | -361.6105 | -0.71846 | -362.329 | 958.0531 | 189.2712 | 123 | 17.5787 | -0.685778810769787-12.9102845810603j | -0.68578 | -12.9103
124 | 174.375 | -325.6676 | -2.4498 | -337.2144 | 33.2127 | 11.5468 | -21.6026 | -1.2957 | -13.1554 | -1.1541 | -0.6169 | 25.3817 | 13.0926 | 38.4743 | -362.5962 | -1.5458 | -364.1419 | 797.8325 | 134.2885 | 124 | 11.6102 | -0.452935526596703-12.704952278435j | -0.45294 | -12.705
125 | 175.7812 | -321.0377 | -1.9203 | -337.928 | 24.9271 | 16.8902 | -17.7404 | -0.97246 | -13.1833 | -0.9478 | -0.90238 | 25.4354 | 19.1513 | 44.5867 | -363.3634 | -2.2611 | -365.6245 | 616.4738 | 81.9323 | 125 | 7.1867 | -0.280367925220721-12.5243308427429j | -0.28037 | -12.5243
126 | 177.1875 | -317.428 | -1.3214 | -338.4379 | 16.6264 | 21.01 | -12.5929 | -0.64863 | -13.2031 | -0.67279 | -1.1225 | 25.4738 | 23.8226 | 49.2964 | -363.9117 | -2.8126 | -366.7243 | 419.4551 | 38.6109 | 126 | 4.0335 | -0.157354796476094-12.3835057886138j | -0.15735 | -12.3835
127 | 178.5938 | -315.1364 | -0.67345 | -338.744 | 8.3157 | 23.6076 | -6.5331 | -0.32441 | -13.2151 | -0.34904 | -1.2613 | 25.4969 | 26.7679 | 52.2648 | -364.2409 | -3.1603 | -367.4012 | 212.2287 | 9.9999 | 127 | 1.7826 | -0.0695427292988557-12.2941089354287j | -0.069543 | -12.2941
128 | 180 | -314.3512 | -3.5435e-15 | -338.8461 | 4.1514e-14 | 24.4949 | -3.6012e-14 | -1.6195e-15 | -13.2191 | -1.924e-15 | -1.3087 | 25.5045 | 27.774 | 53.2785 | -364.3506 | -3.2791 | -367.6297 | 1.1139e-12 | 5.6094e-28 | 128 | 5.5018e-15 | -2.14636817988043E-16-12.2634748458167j | -2.1464e-16 | -12.2635
129 | 181.4062 | -315.1364 | 0.67345 | -338.744 | -8.3157 | 23.6076 | 6.5331 | 0.32441 | -13.2151 | 0.34904 | -1.2613 | 25.4969 | 26.7679 | 52.2648 | -364.2409 | -3.1603 | -367.4012 | -212.2287 | 9.9999 | 129 | -1.7826 | 0.0695427292988491-12.2941089354287j | 0.069543 | -12.2941
130 | 182.8125 | -317.428 | 1.3214 | -338.4379 | -16.6264 | 21.01 | 12.5929 | 0.64863 | -13.2031 | 0.67279 | -1.1225 | 25.4738 | 23.8226 | 49.2964 | -363.9117 | -2.8126 | -366.7243 | -419.4551 | 38.6109 | 130 | -4.0335 | 0.157354796476093-12.3835057886138j | 0.15735 | -12.3835
131 | 184.2188 | -321.0377 | 1.9203 | -337.928 | -24.9271 | 16.8902 | 17.7404 | 0.97246 | -13.1833 | 0.9478 | -0.90238 | 25.4354 | 19.1513 | 44.5867 | -363.3634 | -2.2611 | -365.6245 | -616.4738 | 81.9323 | 131 | -7.1867 | 0.280367925220715-12.5243308427429j | 0.28037 | -12.5243
132 | 185.625 | -325.6676 | 2.4498 | -337.2144 | -33.2127 | 11.5468 | 21.6026 | 1.2957 | -13.1554 | 1.1541 | -0.6169 | 25.3817 | 13.0926 | 38.4743 | -362.5962 | -1.5458 | -364.1419 | -797.8325 | 134.2885 | 132 | -11.6102 | 0.452935526596703-12.704952278435j | 0.45294 | -12.705
133 | 187.0312 | -330.9309 | 2.895 | -336.2978 | -41.4784 | 5.3669 | 23.8997 | 1.6182 | -13.1197 | 1.2769 | -0.28673 | 25.3127 | 6.0853 | 31.3981 | -361.6105 | -0.71846 | -362.329 | -958.0531 | 189.2712 | 133 | -17.5787 | 0.685778810769783-12.9102845810603j | 0.68578 | -12.9103
134 | 188.4375 | -336.3805 | 3.2467 | -335.1786 | -49.719 | -1.2019 | 24.4654 | 1.9396 | -13.076 | 1.3071 | 0.064213 | 25.2285 | -1.3628 | 23.8657 | -360.4071 | 0.1609 | -360.2462 | -1092.137 | 240.8569 | 134 | -25.2537 | 0.985196069297548-13.1228826587699j | 0.9852 | -13.1229
135 | 189.8438 | -341.5411 | 3.5026 | -333.8575 | -57.9298 | -7.6836 | 23.2586 | 2.26 | -13.0245 | 1.2426 | 0.4105 | 25.1291 | -8.7122 | 16.4169 | -358.9865 | 1.0286 | -357.9579 | -1196.2726 | 284.3682 | 135 | -34.6712 | 1.35259242222151-13.3242072498075j | 1.3526 | -13.3242
136 | 191.25 | -345.9439 | 3.667 | -332.3352 | -66.1056 | -13.6086 | 20.3668 | 2.5789 | -12.9651 | 1.0881 | 0.72706 | 25.0145 | -15.4304 | 9.5841 | -357.3497 | 1.8218 | -355.528 | -1268.5864 | 317.0967 | 136 | -45.7388 | 1.78436410718814-13.4959699421067j | 1.7844 | -13.496
137 | 192.6562 | -349.1606 | 3.7511 | -330.6128 | -74.2416 | -18.5478 | 15.9994 | 2.8963 | -12.8979 | 0.85479 | 0.99093 | 24.8848 | -21.0307 | 3.8541 | -355.4977 | 2.483 | -353.0147 | -1309.7364 | 338.503 | 137 | -58.2422 | 2.27214570198609-13.6214603602359j | 2.2721 | -13.6215
138 | 194.0625 | -350.8344 | 3.7715 | -328.6913 | -82.3329 | -22.1431 | 10.4729 | 3.212 | -12.8229 | 0.55953 | 1.183 | 24.7402 | -25.1074 | -0.36719 | -353.4315 | 2.9643 | -350.4672 | -1323.1717 | 350.017 | 138 | -71.86 | 2.80340237810369-13.6867593664786j | 2.8034 | -13.6868
139 | 195.4688 | -350.706 | 3.7494 | -326.5717 | -90.3746 | -24.1343 | 4.1877 | 3.5257 | -12.7402 | 0.22373 | 1.2894 | 24.5807 | -27.3651 | -2.7844 | -351.1524 | 3.2308 | -347.9216 | -1314.9466 | 354.5543 | 139 | -86.1869 | 3.36232428611388-13.681750380672j | 3.3623 | -13.6818
140 | 196.875 | -348.6324 | 3.709 | -324.2555 | -98.3618 | -24.3769 | -2.4009 | 3.8373 | -12.6499 | -0.12827 | 1.3024 | 24.4063 | -27.6403 | -3.2339 | -348.6618 | 3.2633 | -345.3985 | -1293.0853 | 355.9211 | 140 | -100.7627 | 3.93095828484596-13.6008555490839j | 3.931 | -13.6009
141 | 198.2812 | -344.5975 | 3.6756 | -321.7439 | -106.2898 | -22.8536 | -8.8156 | 4.1466 | -12.5519 | -0.47098 | 1.221 | 24.2173 | -25.9129 | -1.6957 | -345.9612 | 3.0594 | -342.9018 | -1266.6018 | 358.2761 | 141 | -115.1054 | 4.49049503120665-13.4434434265073j | 4.4905 | -13.4434
142 | 199.6875 | -338.713 | 3.6738 | -319.0385 | -114.1538 | -19.6745 | -14.5916 | 4.4534 | -12.4463 | -0.77957 | 1.0511 | 24.0137 | -22.3083 | 1.7054 | -343.0522 | 2.6338 | -340.4184 | -1244.3634 | 365.7715 | 142 | -128.7454 | 5.02261819191491-13.2138786337207j | 5.0226 | -13.2139
143 | 201.0938 | -331.211 | 3.7258 | -316.141 | -121.949 | -15.07 | -19.3105 | 4.7575 | -12.3333 | -1.0317 | 0.80513 | 23.7956 | -17.0874 | 6.7081 | -339.9365 | 2.0174 | -337.9191 | -1234.0242 | 382.4102 | 143 | -141.2595 | 5.51081803775923-12.9212098903788j | 5.5108 | -12.9212
144 | 202.5 | -322.4268 | 3.8497 | -313.053 | -129.6708 | -9.3738 | -22.6303 | 5.0587 | -12.2128 | -1.2091 | 0.50081 | 23.5631 | -10.6286 | 12.9345 | -336.6161 | 1.2549 | -335.3612 | -1241.2362 | 412.0703 | 144 | -152.3011 | 5.94157426133595-12.5785190221329j | 5.9416 | -12.5785
145 | 203.9062 | -312.7748 | 4.0581 | -309.7764 | -137.3144 | -2.9984 | -24.3107 | 5.3569 | -12.085 | -1.2988 | 0.16019 | 23.3165 | -3.3998 | 19.9167 | -333.0929 | 0.4014 | -332.6915 | -1269.2679 | 458.5792 | 145 | -161.6251 | 6.30532233364239-12.2019781022758j | 6.3053 | -12.202
146 | 205.3125 | -302.7191 | 4.3574 | -306.3132 | -144.8754 | 3.5941 | -24.2298 | 5.6519 | -11.9499 | -1.2945 | -0.19202 | 23.0558 | 4.0753 | 27.1311 | -329.3691 | -0.48114 | -329.8502 | -1319.0616 | 525.6985 | 146 | -169.1051 | 6.59713339697727-11.8096830330427j | 6.5971 | -11.8097
147 | 206.7188 | -292.7392 | 4.747 | -302.6656 | -152.349 | 9.9263 | -22.3935 | 5.9434 | -11.8076 | -1.1964 | -0.53033 | 22.7813 | 11.2552 | 34.0365 | -325.4468 | -1.3288 | -326.7757 | -1389.647 | 616.9053 | 147 | -174.7425 | 6.81705844520963-11.4203480679754j | 6.8171 | -11.4203
148 | 208.125 | -283.2962 | 5.2198 | -298.8356 | -159.7309 | 15.5394 | -18.9348 | 6.2314 | -11.6582 | -1.0116 | -0.83021 | 22.493 | 17.6196 | 40.1126 | -321.3286 | -2.0802 | -323.4088 | -1478.7531 | 734.9295 | 148 | -178.6657 | 6.97011186406304-11.0519558510903j | 6.9701 | -11.052
149 | 209.5312 | -274.7989 | 5.7621 | -294.8256 | -167.0166 | 20.0267 | -14.1044 | 6.5157 | -11.5017 | -0.75354 | -1.0699 | 22.1912 | 22.7076 | 44.8988 | -317.0167 | -2.6809 | -319.6977 | -1583.4229 | 881.098 | 149 | -181.121 | 7.06589553157611-10.7204607711128j | 7.0659 | -10.7205
150 | 210.9375 | -267.575 | 6.3551 | -290.638 | -174.2017 | 23.063 | -8.2521 | 6.796 | -11.3384 | -0.44088 | -1.2322 | 21.876 | 26.1504 | 48.0264 | -312.514 | -3.0874 | -315.6014 | -1700.4612 | 1054.6237 | 150 | -182.4538 | 7.11789071945929-10.4386395662893j | 7.1179 | -10.4386
151 | 212.3438 | -261.8468 | 6.9759 | -286.2753 | -181.2818 | 24.4285 | -1.802 | 7.0722 | -11.1682 | -0.096272 | -1.3051 | 21.5476 | 27.6987 | 49.2464 | -307.8229 | -3.2702 | -311.0931 | -1826.6169 | 1252.0337 | 151 | -183.0838 | 7.14246910309399-10.2151724471152j | 7.1425 | -10.2152
152 | 213.75 | -257.716 | 7.5994 | -281.7402 | -188.2528 | 24.0242 | 4.7787 | 7.3441 | -10.9913 | 0.25531 | -1.2835 | 21.2063 | 27.2403 | 48.4466 | -302.9465 | -3.2161 | -306.1626 | -1958.4946 | 1466.9295 | 152 | -183.4741 | 7.15769453779935-10.0540213035977j | 7.1577 | -10.054
153 | 215.1562 | -255.156 | 8.2 | -277.0354 | -195.1103 | 21.8794 | 11.0132 | 7.6116 | -10.8077 | 0.58839 | -1.1689 | 20.8521 | 24.8084 | 45.6605 | -297.8875 | -2.929 | -300.8165 | -2092.2893 | 1690.2213 | 153 | -184.0972 | 7.18200241743061-9.95415004035602j | 7.182 | -9.9542
154 | 216.5625 | -254.0142 | 8.7534 | -272.1637 | -201.8504 | 18.1495 | 16.4498 | 7.8746 | -10.6177 | 0.87885 | -0.96966 | 20.4854 | 20.5792 | 41.0646 | -292.6492 | -2.4297 | -295.0788 | -2223.4976 | 1910.8767 | 154 | -185.4006 | 7.23285230016258-9.90960729624546j | 7.2329 | -9.9096
155 | 217.9688 | -254.0234 | 9.2384 | -267.1281 | -208.4688 | 13.1047 | 20.6946 | 8.1328 | -10.4212 | 1.1056 | -0.70013 | 20.1064 | 14.859 | 34.9654 | -287.2345 | -1.7543 | -288.9888 | -2346.7751 | 2117.1082 | 155 | -187.7742 | 7.32545142293852-9.90996555103488j | 7.3255 | -9.91
156 | 219.375 | -254.8211 | 9.6384 | -261.9316 | -214.9617 | 7.1105 | 23.4402 | 8.3861 | -10.2185 | 1.2523 | -0.37989 | 19.7153 | 8.0624 | 27.7776 | -281.6468 | -0.95187 | -282.5987 | -2456.0688 | 2297.8135 | 156 | -191.5215 | 7.47164159021512-9.94108480200865j | 7.4716 | -9.9411
157 | 220.7812 | -255.9761 | 9.9426 | -256.5773 | -221.3251 | 0.60113 | 24.4875 | 8.6343 | -10.0096 | 1.3083 | -0.032116 | 19.3123 | 0.68161 | 19.9939 | -275.8895 | -0.080473 | -275.97 | -2545.0708 | 2444.0187 | 157 | -196.8375 | 7.67903008639606-9.98614547879741j | 7.679 | -9.9861
158 | 222.1875 | -257.0202 | 10.1468 | -251.0684 | -227.5551 | -5.9518 | 23.7608 | 8.8774 | -9.7947 | 1.2694 | 0.31798 | 18.8976 | -6.7485 | 12.1491 | -269.966 | 0.79676 | -269.1692 | -2607.9406 | 2550.0608 | 158 | -203.7943 | 7.95042758222663-10.0268757588386j | 7.9504 | -10.0269
159 | 223.5938 | -257.4818 | 10.2537 | -245.4083 | -233.6481 | -12.0735 | 21.3127 | 9.1151 | -9.5739 | 1.1387 | 0.64504 | 18.4716 | -13.6898 | 4.7818 | -263.8799 | 1.6163 | -262.2636 | -2640.1509 | 2614.3015 | 159 | -212.3354 | 8.28363376423581-10.044884361793j | 8.2836 | -10.0449
160 | 225 | -256.9209 | 10.2727 | -239.6004 | -239.6004 | -17.3205 | 17.3205 | 9.3473 | -9.3473 | 0.92537 | 0.92537 | 18.0344 | -19.6392 | -1.6047 | -257.6348 | 2.3187 | -255.3161 | -2639.2611 | 2639.2611 | 160 | -222.2799 | 8.67158622438762-10.0230022593571j | 8.6716 | -10.023
161 | 226.4062 | -254.9608 | 10.2189 | -233.6481 | -245.4083 | -21.3127 | 12.0735 | 9.5739 | -9.1151 | 0.64504 | 1.1387 | 17.5864 | -24.1658 | -6.5794 | -251.2345 | 2.8531 | -248.3814 | -2605.4222 | 2631.1838 | 161 | -233.3348 | 9.10286182953971-9.94653609085408j | 9.1029 | -9.9465
162 | 227.8125 | -251.3159 | 10.1127 | -227.5551 | -251.0684 | -23.7608 | 5.9518 | 9.7947 | -8.8774 | 0.31798 | 1.2694 | 17.1278 | -26.9416 | -9.8138 | -244.6829 | 3.1808 | -241.5021 | -2541.4739 | 2599.1588 | 162 | -245.1166 | 9.56249425375669-9.80434247155764j | 9.5625 | -9.8043
163 | 229.2188 | -245.8126 | 9.9775 | -221.3251 | -256.5773 | -24.4875 | -0.60113 | 10.0096 | -8.6343 | -0.032116 | 1.3083 | 16.6589 | -27.7656 | -11.1068 | -237.9839 | 3.2781 | -234.7058 | -2452.5902 | 2553.9967 | 163 | -257.1784 | 10.0330484510586-9.58964535649586j | 10.033 | -9.5896
164 | 230.625 | -238.4018 | 9.8386 | -214.9617 | -261.9316 | -23.4402 | -7.1105 | 10.2185 | -8.3861 | -0.37989 | 1.2523 | 16.1799 | -26.5781 | -10.3981 | -231.1416 | 3.1379 | -228.0037 | -2345.5387 | 2507.0809 | 164 | -269.0421 | 10.4958742312507-9.30053723741499j | 10.4959 | -9.3005
165 | 232.0312 | -229.1634 | 9.7211 | -208.4688 | -267.1281 | -20.6946 | -13.1047 | 10.4212 | -8.1328 | -0.70013 | 1.1056 | 15.6912 | -23.465 | -7.7738 | -224.16 | 2.7704 | -221.3897 | -2227.7143 | 2469.3799 | 165 | -280.2328 | 10.9324481256932-8.94012785605618j | 10.9324 | -8.9401
166 | 233.4375 | -218.3001 | 9.648 | -201.8504 | -272.1637 | -16.4498 | -18.1495 | 10.6177 | -7.8746 | -0.96966 | 0.87885 | 15.193 | -18.6519 | -3.4588 | -217.0434 | 2.2021 | -214.8413 | -2106.1595 | 2450.7287 | 166 | -290.3132 | 11.3257063333006-8.51632965344822j | 11.3257 | -8.5163
167 | 234.8438 | -206.1235 | 9.6388 | -195.1103 | -277.0354 | -11.0132 | -21.8794 | 10.8077 | -7.6116 | -1.1689 | 0.58839 | 14.6857 | -12.4875 | 2.1982 | -209.7961 | 1.4743 | -208.3218 | -1986.779 | 2459.3918 | 167 | -298.9148 | 11.661272183117-8.04129549248728j | 11.6613 | -8.0413
168 | 236.25 | -193.0315 | 9.7077 | -188.2528 | -281.7402 | -4.7787 | -24.0242 | 10.9913 | -7.3441 | -1.2835 | 0.25531 | 14.1696 | -5.4184 | 8.7511 | -202.4224 | 0.63972 | -201.7826 | -1873.8986 | 2501.8382 | 168 | -305.7645 | 11.9284891917076-7.53054938300047j | 11.9285 | -7.5305
169 | 237.6562 | -179.4799 | 9.8631 | -181.2818 | -286.2753 | 1.802 | -24.4285 | 11.1682 | -7.0722 | -1.3051 | -0.096272 | 13.6449 | 2.0432 | 15.6881 | -194.9267 | -0.24123 | -195.1679 | -1770.2205 | 2582.61 | 169 | -310.7038 | 12.1211848776791-7.00187317967868j | 12.1212 | -7.0019
170 | 239.0625 | -165.9496 | 10.1062 | -174.2017 | -290.638 | 8.2521 | -23.063 | 11.3384 | -6.796 | -1.2322 | -0.44088 | 13.112 | 9.3568 | 22.4687 | -187.3137 | -1.1047 | -188.4184 | -1677.1212 | 2704.1679 | 170 | -313.701 | 12.2381100015517-6.47402990238611j | 12.2381 | -6.474
171 | 240.4688 | -152.9123 | 10.4318 | -167.0166 | -294.8256 | 14.1044 | -20.0267 | 11.5017 | -6.5157 | -1.0699 | -0.75354 | 12.5711 | 15.9925 | 28.5636 | -179.5878 | -1.8881 | -181.4759 | -1595.1493 | 2866.6459 | 171 | -314.8522 | 12.2830214137735-5.96541616459409j | 12.283 | -5.9654
172 | 241.875 | -140.7961 | 10.828 | -159.7309 | -298.8356 | 18.9348 | -15.5394 | 11.6582 | -6.2314 | -0.83021 | -1.0116 | 12.0228 | 21.4696 | 33.4924 | -171.7537 | -2.5348 | -174.2885 | -1524.5362 | 3067.5223 | 172 | -314.375 | 12.2644025133287-5.49274133153827j | 12.2644 | -5.4927
173 | 243.2812 | -129.9556 | 11.2773 | -152.349 | -302.6656 | 22.3935 | -9.9263 | 11.8076 | -5.9434 | -0.53033 | -1.1964 | 11.4671 | 25.3913 | 36.8584 | -163.8162 | -2.9978 | -166.814 | -1465.5438 | 3301.2988 | 173 | -312.5919 | 12.1948415735524-5.06982909307394j | 12.1948 | -5.0698
174 | 244.6875 | -120.6456 | 11.7579 | -144.8754 | -306.3132 | 24.2298 | -3.5941 | 11.9499 | -5.6519 | -0.19202 | -1.2945 | 10.9046 | 27.4734 | 38.378 | -155.78 | -3.2436 | -159.0236 | -1418.536 | 3559.3336 | 174 | -309.9074 | 12.0901129783827-4.7066282674148j | 12.0901 | -4.7066
175 | 246.0938 | -113.0037 | 12.2452 | -137.3144 | -309.7764 | 24.3107 | 2.9984 | 12.085 | -5.3569 | 0.16019 | -1.2988 | 10.3355 | 27.5651 | 37.9006 | -147.6499 | -3.2544 | -150.9044 | -1383.7532 | 3829.9897 | 175 | -306.778 | 11.9680279356008-4.40850449350643j | 11.968 | -4.4085
176 | 247.5 | -107.0404 | 12.7136 | -129.6708 | -313.053 | 22.6303 | 9.3738 | 12.2128 | -5.0587 | 0.50081 | -1.2091 | 9.7602 | 25.6598 | 35.42 | -139.4309 | -3.0295 | -142.4604 | -1360.873 | 4099.2156 | 176 | -303.6792 | 11.8471379343324-4.17586411990473j | 11.8471 | -4.1759
177 | 248.9062 | -102.6386 | 13.1384 | -121.949 | -316.141 | 19.3105 | 15.07 | 12.3333 | -4.7575 | 0.80513 | -1.0317 | 9.179 | 21.8955 | 31.0745 | -131.128 | -2.5851 | -133.7131 | -1348.5096 | 4351.5926 | 177 | -301.0709 | 11.7453848822588-4.00413753100779j | 11.7454 | -4.0041
178 | 250.3125 | -99.5622 | 13.4975 | -114.1538 | -319.0385 | 14.5916 | 19.6745 | 12.4463 | -4.4534 | 1.0511 | -0.77957 | 8.5922 | 16.545 | 25.1372 | -122.746 | -1.9534 | -124.6994 | -1343.8378 | 4571.768 | 178 | -299.364 | 11.6787957207415-3.884123110931j | 11.6788 | -3.8841
179 | 251.7188 | -97.4742 | 13.7729 | -106.2898 | -321.7439 | 8.8156 | 22.8536 | 12.5519 | -4.1466 | 1.221 | -0.47098 | 8.0003 | 9.9957 | 17.996 | -114.2901 | -1.1801 | -115.4703 | -1342.4987 | 4746.0914 | 179 | -298.8903 | 11.6603160935455-3.8026669178018j | 11.6603 | -3.8027
180 | 253.125 | -95.9609 | 13.9522 | -98.3618 | -324.2555 | 2.4009 | 24.3769 | 12.6499 | -3.8373 | 1.3024 | -0.12827 | 7.4036 | 2.7223 | 10.1259 | -105.7654 | -0.32141 | -106.0868 | -1338.8683 | 4864.1987 | 180 | -299.8785 | 11.6988675705147-3.74362881966824j | 11.6989 | -3.7436
181 | 254.5312 | -94.5623 | 14.0296 | -90.3746 | -326.5717 | -4.1877 | 24.1343 | 12.7402 | -3.5257 | 1.2894 | 0.22373 | 6.8024 | -4.7483 | 2.0541 | -97.177 | 0.5606 | -96.6164 | -1326.673 | 4920.2735 | 181 | -302.4375 | 11.7986967312825-3.68906508960562j | 11.7987 | -3.6891
182 | 255.9375 | -92.8058 | 14.0059 | -82.3329 | -328.6913 | -10.4729 | 22.1431 | 12.8229 | -3.212 | 1.183 | 0.55953 | 6.1971 | -11.8749 | -5.6778 | -88.53 | 1.402 | -87.128 | -1299.8317 | 4913.763 | 182 | -306.5482 | 11.9590632692671-3.62054177552962j | 11.9591 | -3.6205
183 | 257.3438 | -90.241 | 13.8888 | -74.2416 | -330.6128 | -15.9994 | 18.5478 | 12.8979 | -2.8963 | 0.99093 | 0.85479 | 5.5881 | -18.1412 | -12.5531 | -79.8297 | 2.1418 | -77.6879 | -1253.34 | 4849.4249 | 183 | -312.0651 | 12.1742897147041-3.5204836858096j | 12.1743 | -3.5205
184 | 258.75 | -86.4724 | 13.6921 | -66.1056 | -332.3352 | -20.3668 | 13.6086 | 12.9651 | -2.5789 | 0.72706 | 1.0881 | 4.9757 | -23.0932 | -18.1175 | -71.0813 | 2.7265 | -68.3548 | -1183.9904 | 4736.7072 | 184 | -318.7266 | 12.4341691767477-3.37346125142709j | 12.4342 | -3.3735
185 | 260.1562 | -81.1884 | 13.435 | -57.9298 | -333.8575 | -23.2586 | 7.6836 | 13.0245 | -2.26 | 0.4105 | 1.2426 | 4.3603 | -26.3722 | -22.0119 | -62.2901 | 3.1136 | -59.1765 | -1090.7623 | 4588.5904 | 185 | -326.1739 | 12.7247015667467-3.16732202608075j | 12.7247 | -3.1673
186 | 261.5625 | -74.1844 | 13.1402 | -49.719 | -335.1786 | -24.4654 | 1.2019 | 13.076 | -1.9396 | 0.064213 | 1.3071 | 3.7423 | -27.7405 | -23.9983 | -53.4613 | 3.2752 | -50.1862 | -974.7989 | 4420.1093 | 186 | -333.9767 | 13.0291049668442-2.89408484123855j | 13.0291 | -2.8941
187 | 262.9688 | -65.3781 | 12.8329 | -41.4784 | -336.2978 | -23.8997 | -5.3669 | 13.1197 | -1.6182 | -0.28673 | 1.2769 | 3.122 | -27.0992 | -23.9771 | -44.6004 | 3.1994 | -41.401 | -838.9923 | 4246.8123 | 187 | -341.6647 | 13.3290288741539-2.55053182823534j | 13.329 | -2.5505
188 | 264.375 | -54.8153 | 12.5385 | -33.2127 | -337.2144 | -21.6026 | -11.5468 | 13.1554 | -1.2957 | -0.6169 | 1.1541 | 2.4999 | -24.4945 | -21.9946 | -35.7126 | 2.8919 | -32.8207 | -687.3024 | 4083.3886 | 188 | -348.7613 | 13.605881425105-2.13845540836193j | 13.6059 | -2.1385
189 | 265.7812 | -42.6674 | 12.2809 | -24.9271 | -337.928 | -17.7404 | -16.8902 | 13.1833 | -0.97246 | -0.90238 | 0.9478 | 1.8762 | -20.1152 | -18.239 | -26.8033 | 2.3749 | -24.4284 | -523.9932 | 3942.6239 | 189 | -354.8182 | 13.8421744467253-1.66454234869056j | 13.8422 | -1.6645
190 | 267.1875 | -29.2193 | 12.0807 | -16.6264 | -338.4379 | -12.5929 | -21.01 | 13.2031 | -0.64863 | -1.1225 | 0.67279 | 1.2514 | -14.2787 | -13.0272 | -17.8778 | 1.6858 | -16.192 | -352.9884 | 3834.7412 | 190 | -359.4479 | 14.0227888899035-1.13990327516373j | 14.0228 | -1.1399
191 | 268.5938 | -14.8488 | 11.9538 | -8.3157 | -338.744 | -6.5331 | -23.6076 | 13.2151 | -0.32441 | -1.2613 | 0.34904 | 0.62591 | -7.4077 | -6.7818 | -8.9416 | 0.87458 | -8.067 | -177.5 | 3767.0864 | 191 | -362.3516 | 14.1360689676182-0.57928172031471j | 14.1361 | -0.57928
192 | 270 | -1.583e-13 | 11.9104 | -6.2271e-14 | -338.8461 | -9.6029e-14 | -24.4949 | 13.2191 | -2.4293e-15 | -1.3087 | 5.1305e-15 | 4.687e-15 | -1.0888e-13 | -1.042e-13 | -6.6958e-14 | 1.2855e-14 | -5.4102e-14 | -1.8854e-12 | 3744.0494 | 192 | -363.341 | 14.174665730879-6.17558302079048E-15j | 14.1747 | -6.1756e-15
193 | 271.4062 | 14.8488 | 11.9538 | 8.3157 | -338.744 | 6.5331 | -23.6076 | 13.2151 | 0.32441 | -1.2613 | -0.34904 | -0.62591 | 7.4077 | 6.7818 | 8.9416 | -0.87458 | 8.067 | 177.5 | 3767.0864 | 193 | -362.3516 | 14.1360689676182+0.57928172031471j | 14.1361 | 0.57928
194 | 272.8125 | 29.2193 | 12.0807 | 16.6264 | -338.4379 | 12.5929 | -21.01 | 13.2031 | 0.64863 | -1.1225 | -0.67279 | -1.2514 | 14.2787 | 13.0272 | 17.8778 | -1.6858 | 16.192 | 352.9884 | 3834.7412 | 194 | -359.4479 | 14.0227888899035+1.13990327516371j | 14.0228 | 1.1399
195 | 274.2188 | 42.6674 | 12.2809 | 24.9271 | -337.928 | 17.7404 | -16.8902 | 13.1833 | 0.97246 | -0.90238 | -0.9478 | -1.8762 | 20.1152 | 18.239 | 26.8033 | -2.3749 | 24.4284 | 523.9932 | 3942.6239 | 195 | -354.8182 | 13.8421744467253+1.66454234869056j | 13.8422 | 1.6645
196 | 275.625 | 54.8153 | 12.5385 | 33.2127 | -337.2144 | 21.6026 | -11.5468 | 13.1554 | 1.2957 | -0.6169 | -1.1541 | -2.4999 | 24.4945 | 21.9946 | 35.7126 | -2.8919 | 32.8207 | 687.3024 | 4083.3886 | 196 | -348.7613 | 13.605881425105+2.13845540836193j | 13.6059 | 2.1385
197 | 277.0312 | 65.3781 | 12.8329 | 41.4784 | -336.2978 | 23.8997 | -5.3669 | 13.1197 | 1.6182 | -0.28673 | -1.2769 | -3.122 | 27.0992 | 23.9771 | 44.6004 | -3.1994 | 41.401 | 838.9923 | 4246.8123 | 197 | -341.6647 | 13.3290288741539+2.55053182823532j | 13.329 | 2.5505
198 | 278.4375 | 74.1844 | 13.1402 | 49.719 | -335.1786 | 24.4654 | 1.2019 | 13.076 | 1.9396 | 0.064213 | -1.3071 | -3.7423 | 27.7405 | 23.9983 | 53.4613 | -3.2752 | 50.1862 | 974.7989 | 4420.1093 | 198 | -333.9767 | 13.0291049668442+2.89408484123856j | 13.0291 | 2.8941
199 | 279.8438 | 81.1884 | 13.435 | 57.9298 | -333.8575 | 23.2586 | 7.6836 | 13.0245 | 2.26 | 0.4105 | -1.2426 | -4.3603 | 26.3722 | 22.0119 | 62.2901 | -3.1136 | 59.1765 | 1090.7623 | 4588.5904 | 199 | -326.1739 | 12.7247015667467+3.16732202608075j | 12.7247 | 3.1673
200 | 281.25 | 86.4724 | 13.6921 | 66.1056 | -332.3352 | 20.3668 | 13.6086 | 12.9651 | 2.5789 | 0.72706 | -1.0881 | -4.9757 | 23.0932 | 18.1175 | 71.0813 | -2.7265 | 68.3548 | 1183.9904 | 4736.7072 | 200 | -318.7266 | 12.4341691767477+3.37346125142709j | 12.4342 | 3.3735
201 | 282.6562 | 90.241 | 13.8888 | 74.2416 | -330.6128 | 15.9994 | 18.5478 | 12.8979 | 2.8963 | 0.99093 | -0.85479 | -5.5881 | 18.1412 | 12.5531 | 79.8297 | -2.1418 | 77.6879 | 1253.34 | 4849.4249 | 201 | -312.0651 | 12.1742897147042+3.5204836858096j | 12.1743 | 3.5205
202 | 284.0625 | 92.8058 | 14.0059 | 82.3329 | -328.6913 | 10.4729 | 22.1431 | 12.8229 | 3.212 | 1.183 | -0.55953 | -6.1971 | 11.8749 | 5.6778 | 88.53 | -1.402 | 87.128 | 1299.8317 | 4913.763 | 202 | -306.5482 | 11.9590632692671+3.62054177552962j | 11.9591 | 3.6205
203 | 285.4688 | 94.5623 | 14.0296 | 90.3746 | -326.5717 | 4.1877 | 24.1343 | 12.7402 | 3.5257 | 1.2894 | -0.22373 | -6.8024 | 4.7483 | -2.0541 | 97.177 | -0.5606 | 96.6164 | 1326.673 | 4920.2735 | 203 | -302.4375 | 11.7986967312825+3.68906508960561j | 11.7987 | 3.6891
204 | 286.875 | 95.9609 | 13.9522 | 98.3618 | -324.2555 | -2.4009 | 24.3769 | 12.6499 | 3.8373 | 1.3024 | 0.12827 | -7.4036 | -2.7223 | -10.1259 | 105.7654 | 0.32141 | 106.0868 | 1338.8683 | 4864.1987 | 204 | -299.8785 | 11.6988675705147+3.74362881966823j | 11.6989 | 3.7436
205 | 288.2812 | 97.4742 | 13.7729 | 106.2898 | -321.7439 | -8.8156 | 22.8536 | 12.5519 | 4.1466 | 1.221 | 0.47098 | -8.0003 | -9.9957 | -17.996 | 114.2901 | 1.1801 | 115.4703 | 1342.4987 | 4746.0914 | 205 | -298.8903 | 11.6603160935455+3.80266691780181j | 11.6603 | 3.8027
206 | 289.6875 | 99.5622 | 13.4975 | 114.1538 | -319.0385 | -14.5916 | 19.6745 | 12.4463 | 4.4534 | 1.0511 | 0.77957 | -8.5922 | -16.545 | -25.1372 | 122.746 | 1.9534 | 124.6994 | 1343.8378 | 4571.768 | 206 | -299.364 | 11.6787957207415+3.88412311093099j | 11.6788 | 3.8841
207 | 291.0938 | 102.6386 | 13.1384 | 121.949 | -316.141 | -19.3105 | 15.07 | 12.3333 | 4.7575 | 0.80513 | 1.0317 | -9.179 | -21.8955 | -31.0745 | 131.128 | 2.5851 | 133.7131 | 1348.5096 | 4351.5926 | 207 | -301.0709 | 11.7453848822588+4.00413753100783j | 11.7454 | 4.0041
208 | 292.5 | 107.0404 | 12.7136 | 129.6708 | -313.053 | -22.6303 | 9.3738 | 12.2128 | 5.0587 | 0.50081 | 1.2091 | -9.7602 | -25.6598 | -35.42 | 139.4309 | 3.0295 | 142.4604 | 1360.873 | 4099.2156 | 208 | -303.6792 | 11.8471379343324+4.17586411990473j | 11.8471 | 4.1759
209 | 293.9062 | 113.0037 | 12.2452 | 137.3144 | -309.7764 | -24.3107 | 2.9984 | 12.085 | 5.3569 | 0.16019 | 1.2988 | -10.3355 | -27.5651 | -37.9006 | 147.6499 | 3.2544 | 150.9044 | 1383.7532 | 3829.9897 | 209 | -306.778 | 11.9680279356008+4.40850449350639j | 11.968 | 4.4085
210 | 295.3125 | 120.6456 | 11.7579 | 144.8754 | -306.3132 | -24.2298 | -3.5941 | 11.9499 | 5.6519 | -0.19202 | 1.2945 | -10.9046 | -27.4734 | -38.378 | 155.78 | 3.2436 | 159.0236 | 1418.536 | 3559.3336 | 210 | -309.9074 | 12.0901129783827+4.7066282674148j | 12.0901 | 4.7066
211 | 296.7188 | 129.9556 | 11.2773 | 152.349 | -302.6656 | -22.3935 | -9.9263 | 11.8076 | 5.9434 | -0.53033 | 1.1964 | -11.4671 | -25.3913 | -36.8584 | 163.8162 | 2.9978 | 166.814 | 1465.5438 | 3301.2988 | 211 | -312.5919 | 12.1948415735524+5.06982909307394j | 12.1948 | 5.0698
212 | 298.125 | 140.7961 | 10.828 | 159.7309 | -298.8356 | -18.9348 | -15.5394 | 11.6582 | 6.2314 | -0.83021 | 1.0116 | -12.0228 | -21.4696 | -33.4924 | 171.7537 | 2.5348 | 174.2885 | 1524.5362 | 3067.5223 | 212 | -314.375 | 12.2644025133287+5.49274133153827j | 12.2644 | 5.4927
213 | 299.5312 | 152.9123 | 10.4318 | 167.0166 | -294.8256 | -14.1044 | -20.0267 | 11.5017 | 6.5157 | -1.0699 | 0.75354 | -12.5711 | -15.9925 | -28.5636 | 179.5878 | 1.8881 | 181.4759 | 1595.1493 | 2866.6459 | 213 | -314.8522 | 12.2830214137735+5.96541616459409j | 12.283 | 5.9654
214 | 300.9375 | 165.9496 | 10.1062 | 174.2017 | -290.638 | -8.2521 | -23.063 | 11.3384 | 6.796 | -1.2322 | 0.44088 | -13.112 | -9.3568 | -22.4687 | 187.3137 | 1.1047 | 188.4184 | 1677.1212 | 2704.1679 | 214 | -313.701 | 12.2381100015517+6.47402990238611j | 12.2381 | 6.474
215 | 302.3438 | 179.4799 | 9.8631 | 181.2818 | -286.2753 | -1.802 | -24.4285 | 11.1682 | 7.0722 | -1.3051 | 0.096272 | -13.6449 | -2.0432 | -15.6881 | 194.9267 | 0.24123 | 195.1679 | 1770.2205 | 2582.61 | 215 | -310.7038 | 12.1211848776791+7.00187317967872j | 12.1212 | 7.0019
216 | 303.75 | 193.0315 | 9.7077 | 188.2528 | -281.7402 | 4.7787 | -24.0242 | 10.9913 | 7.3441 | -1.2835 | -0.25531 | -14.1696 | 5.4184 | -8.7511 | 202.4224 | -0.63972 | 201.7826 | 1873.8986 | 2501.8382 | 216 | -305.7645 | 11.9284891917076+7.53054938300047j | 11.9285 | 7.5305
217 | 305.1562 | 206.1235 | 9.6388 | 195.1103 | -277.0354 | 11.0132 | -21.8794 | 10.8077 | 7.6116 | -1.1689 | -0.58839 | -14.6857 | 12.4875 | -2.1982 | 209.7961 | -1.4743 | 208.3218 | 1986.779 | 2459.3918 | 217 | -298.9148 | 11.661272183117+8.04129549248728j | 11.6613 | 8.0413
218 | 306.5625 | 218.3001 | 9.648 | 201.8504 | -272.1637 | 16.4498 | -18.1495 | 10.6177 | 7.8746 | -0.96966 | -0.87885 | -15.193 | 18.6519 | 3.4588 | 217.0434 | -2.2021 | 214.8413 | 2106.1595 | 2450.7287 | 218 | -290.3132 | 11.3257063333006+8.51632965344819j | 11.3257 | 8.5163
219 | 307.9688 | 229.1634 | 9.7211 | 208.4688 | -267.1281 | 20.6946 | -13.1047 | 10.4212 | 8.1328 | -0.70013 | -1.1056 | -15.6912 | 23.465 | 7.7738 | 224.16 | -2.7704 | 221.3897 | 2227.7143 | 2469.3799 | 219 | -280.2328 | 10.9324481256932+8.94012785605618j | 10.9324 | 8.9401
220 | 309.375 | 238.4018 | 9.8386 | 214.9617 | -261.9316 | 23.4402 | -7.1105 | 10.2185 | 8.3861 | -0.37989 | -1.2523 | -16.1799 | 26.5781 | 10.3981 | 231.1416 | -3.1379 | 228.0037 | 2345.5387 | 2507.0809 | 220 | -269.0421 | 10.4958742312507+9.30053723741499j | 10.4959 | 9.3005
221 | 310.7812 | 245.8126 | 9.9775 | 221.3251 | -256.5773 | 24.4875 | -0.60113 | 10.0096 | 8.6343 | -0.032116 | -1.3083 | -16.6589 | 27.7656 | 11.1068 | 237.9839 | -3.2781 | 234.7058 | 2452.5902 | 2553.9967 | 221 | -257.1784 | 10.0330484510586+9.58964535649586j | 10.033 | 9.5896
222 | 312.1875 | 251.3159 | 10.1127 | 227.5551 | -251.0684 | 23.7608 | 5.9518 | 9.7947 | 8.8774 | 0.31798 | -1.2694 | -17.1278 | 26.9416 | 9.8138 | 244.6829 | -3.1808 | 241.5021 | 2541.4739 | 2599.1588 | 222 | -245.1166 | 9.56249425375669+9.80434247155764j | 9.5625 | 9.8043
223 | 313.5938 | 254.9608 | 10.2189 | 233.6481 | -245.4083 | 21.3127 | 12.0735 | 9.5739 | 9.1151 | 0.64504 | -1.1387 | -17.5864 | 24.1658 | 6.5794 | 251.2345 | -2.8531 | 248.3814 | 2605.4222 | 2631.1838 | 223 | -233.3348 | 9.10286182953971+9.94653609085408j | 9.1029 | 9.9465
224 | 315 | 256.9209 | 10.2727 | 239.6004 | -239.6004 | 17.3205 | 17.3205 | 9.3473 | 9.3473 | 0.92537 | -0.92537 | -18.0344 | 19.6392 | 1.6047 | 257.6348 | -2.3187 | 255.3161 | 2639.2611 | 2639.2611 | 224 | -222.2799 | 8.67158622438762+10.0230022593571j | 8.6716 | 10.023
225 | 316.4062 | 257.4818 | 10.2537 | 245.4083 | -233.6481 | 12.0735 | 21.3127 | 9.1151 | 9.5739 | 1.1387 | -0.64504 | -18.4716 | 13.6898 | -4.7818 | 263.8799 | -1.6163 | 262.2636 | 2640.1509 | 2614.3015 | 225 | -212.3354 | 8.28363376423581+10.044884361793j | 8.2836 | 10.0449
226 | 317.8125 | 257.0202 | 10.1468 | 251.0684 | -227.5551 | 5.9518 | 23.7608 | 8.8774 | 9.7947 | 1.2694 | -0.31798 | -18.8976 | 6.7485 | -12.1491 | 269.966 | -0.79676 | 269.1692 | 2607.9406 | 2550.0608 | 226 | -203.7943 | 7.95042758222663+10.0268757588386j | 7.9504 | 10.0269
227 | 319.2188 | 255.9761 | 9.9426 | 256.5773 | -221.3251 | -0.60113 | 24.4875 | 8.6343 | 10.0096 | 1.3083 | 0.032116 | -19.3123 | -0.68161 | -19.9939 | 275.8895 | 0.080473 | 275.97 | 2545.0708 | 2444.0187 | 227 | -196.8375 | 7.6790300863961+9.98614547879738j | 7.679 | 9.9861
228 | 320.625 | 254.8211 | 9.6384 | 261.9316 | -214.9617 | -7.1105 | 23.4402 | 8.3861 | 10.2185 | 1.2523 | 0.37989 | -19.7153 | -8.0624 | -27.7776 | 281.6468 | 0.95187 | 282.5987 | 2456.0688 | 2297.8135 | 228 | -191.5215 | 7.47164159021512+9.94108480200865j | 7.4716 | 9.9411
229 | 322.0312 | 254.0234 | 9.2384 | 267.1281 | -208.4688 | -13.1047 | 20.6946 | 8.1328 | 10.4212 | 1.1056 | 0.70013 | -20.1064 | -14.859 | -34.9654 | 287.2345 | 1.7543 | 288.9888 | 2346.7751 | 2117.1082 | 229 | -187.7742 | 7.32545142293852+9.90996555103492j | 7.3255 | 9.91
230 | 323.4375 | 254.0142 | 8.7534 | 272.1637 | -201.8504 | -18.1495 | 16.4498 | 7.8746 | 10.6177 | 0.87885 | 0.96966 | -20.4854 | -20.5792 | -41.0646 | 292.6492 | 2.4297 | 295.0788 | 2223.4976 | 1910.8767 | 230 | -185.4006 | 7.23285230016258+9.90960729624546j | 7.2329 | 9.9096
231 | 324.8438 | 255.156 | 8.2 | 277.0354 | -195.1103 | -21.8794 | 11.0132 | 7.6116 | 10.8077 | 0.58839 | 1.1689 | -20.8521 | -24.8084 | -45.6605 | 297.8875 | 2.929 | 300.8165 | 2092.2893 | 1690.2213 | 231 | -184.0972 | 7.18200241743065+9.95415004035598j | 7.182 | 9.9542
232 | 326.25 | 257.716 | 7.5994 | 281.7402 | -188.2528 | -24.0242 | 4.7787 | 7.3441 | 10.9913 | 0.25531 | 1.2835 | -21.2063 | -27.2403 | -48.4466 | 302.9465 | 3.2161 | 306.1626 | 1958.4946 | 1466.9295 | 232 | -183.4741 | 7.15769453779935+10.0540213035977j | 7.1577 | 10.054
233 | 327.6562 | 261.8468 | 6.9759 | 286.2753 | -181.2818 | -24.4285 | -1.802 | 7.0722 | 11.1682 | -0.096272 | 1.3051 | -21.5476 | -27.6987 | -49.2464 | 307.8229 | 3.2702 | 311.0931 | 1826.6169 | 1252.0337 | 233 | -183.0838 | 7.14246910309399+10.2151724471152j | 7.1425 | 10.2152
234 | 329.0625 | 267.575 | 6.3551 | 290.638 | -174.2017 | -23.063 | -8.2521 | 6.796 | 11.3384 | -0.44088 | 1.2322 | -21.876 | -26.1504 | -48.0264 | 312.514 | 3.0874 | 315.6014 | 1700.4612 | 1054.6237 | 234 | -182.4538 | 7.11789071945933+10.4386395662893j | 7.1179 | 10.4386
235 | 330.4688 | 274.7989 | 5.7621 | 294.8256 | -167.0166 | -20.0267 | -14.1044 | 6.5157 | 11.5017 | -0.75354 | 1.0699 | -22.1912 | -22.7076 | -44.8988 | 317.0167 | 2.6809 | 319.6977 | 1583.4229 | 881.098 | 235 | -181.121 | 7.06589553157611+10.7204607711128j | 7.0659 | 10.7205
236 | 331.875 | 283.2962 | 5.2198 | 298.8356 | -159.7309 | -15.5394 | -18.9348 | 6.2314 | 11.6582 | -1.0116 | 0.83021 | -22.493 | -17.6196 | -40.1126 | 321.3286 | 2.0802 | 323.4088 | 1478.7531 | 734.9295 | 236 | -178.6657 | 6.97011186406304+11.0519558510903j | 6.9701 | 11.052
237 | 333.2812 | 292.7392 | 4.747 | 302.6656 | -152.349 | -9.9263 | -22.3935 | 5.9434 | 11.8076 | -1.1964 | 0.53033 | -22.7813 | -11.2552 | -34.0365 | 325.4468 | 1.3288 | 326.7757 | 1389.647 | 616.9053 | 237 | -174.7425 | 6.81705844520963+11.4203480679754j | 6.8171 | 11.4203
238 | 334.6875 | 302.7191 | 4.3574 | 306.3132 | -144.8754 | -3.5941 | -24.2298 | 5.6519 | 11.9499 | -1.2945 | 0.19202 | -23.0558 | -4.0753 | -27.1311 | 329.3691 | 0.48114 | 329.8502 | 1319.0616 | 525.6985 | 238 | -169.1051 | 6.59713339697727+11.8096830330427j | 6.5971 | 11.8097
239 | 336.0938 | 312.7748 | 4.0581 | 309.7764 | -137.3144 | 2.9984 | -24.3107 | 5.3569 | 12.085 | -1.2988 | -0.16019 | -23.3165 | 3.3998 | -19.9167 | 333.0929 | -0.4014 | 332.6915 | 1269.2679 | 458.5792 | 239 | -161.6251 | 6.30532233364239+12.2019781022758j | 6.3053 | 12.202
240 | 337.5 | 322.4268 | 3.8497 | 313.053 | -129.6708 | 9.3738 | -22.6303 | 5.0587 | 12.2128 | -1.2091 | -0.50081 | -23.5631 | 10.6286 | -12.9345 | 336.6161 | -1.2549 | 335.3612 | 1241.2362 | 412.0703 | 240 | -152.3011 | 5.94157426133595+12.5785190221329j | 5.9416 | 12.5785
241 | 338.9062 | 331.211 | 3.7258 | 316.141 | -121.949 | 15.07 | -19.3105 | 4.7575 | 12.3333 | -1.0317 | -0.80513 | -23.7956 | 17.0874 | -6.7081 | 339.9365 | -2.0174 | 337.9191 | 1234.0242 | 382.4102 | 241 | -141.2595 | 5.51081803775927+12.9212098903788j | 5.5108 | 12.9212
242 | 340.3125 | 338.713 | 3.6738 | 319.0385 | -114.1538 | 19.6745 | -14.5916 | 4.4534 | 12.4463 | -0.77957 | -1.0511 | -24.0137 | 22.3083 | -1.7054 | 343.0522 | -2.6338 | 340.4184 | 1244.3634 | 365.7715 | 242 | -128.7454 | 5.02261819191491+13.2138786337207j | 5.0226 | 13.2139
243 | 341.7188 | 344.5975 | 3.6756 | 321.7439 | -106.2898 | 22.8536 | -8.8156 | 4.1466 | 12.5519 | -0.47098 | -1.221 | -24.2173 | 25.9129 | 1.6957 | 345.9612 | -3.0594 | 342.9018 | 1266.6018 | 358.2761 | 243 | -115.1054 | 4.49049503120665+13.4434434265073j | 4.4905 | 13.4434
244 | 343.125 | 348.6324 | 3.709 | 324.2555 | -98.3618 | 24.3769 | -2.4009 | 3.8373 | 12.6499 | -0.12827 | -1.3024 | -24.4063 | 27.6403 | 3.2339 | 348.6618 | -3.2633 | 345.3985 | 1293.0853 | 355.9211 | 244 | -100.7627 | 3.930958284846+13.6008555490838j | 3.931 | 13.6009
245 | 344.5312 | 350.706 | 3.7494 | 326.5717 | -90.3746 | 24.1343 | 4.1877 | 3.5257 | 12.7402 | 0.22373 | -1.2894 | -24.5807 | 27.3651 | 2.7844 | 351.1524 | -3.2308 | 347.9216 | 1314.9466 | 354.5543 | 245 | -86.1869 | 3.3623242861139+13.681750380672j | 3.3623 | 13.6818
246 | 345.9375 | 350.8344 | 3.7715 | 328.6913 | -82.3329 | 22.1431 | 10.4729 | 3.212 | 12.8229 | 0.55953 | -1.183 | -24.7402 | 25.1074 | 0.36719 | 353.4315 | -2.9643 | 350.4672 | 1323.1717 | 350.017 | 246 | -71.86 | 2.80340237810369+13.6867593664786j | 2.8034 | 13.6868
247 | 347.3438 | 349.1606 | 3.7511 | 330.6128 | -74.2416 | 18.5478 | 15.9994 | 2.8963 | 12.8979 | 0.85479 | -0.99093 | -24.8848 | 21.0307 | -3.8541 | 355.4977 | -2.483 | 353.0147 | 1309.7364 | 338.503 | 247 | -58.2422 | 2.27214570198607+13.6214603602359j | 2.2721 | 13.6215
248 | 348.75 | 345.9439 | 3.667 | 332.3352 | -66.1056 | 13.6086 | 20.3668 | 2.5789 | 12.9651 | 1.0881 | -0.72706 | -25.0145 | 15.4304 | -9.5841 | 357.3497 | -1.8218 | 355.528 | 1268.5864 | 317.0967 | 248 | -45.7388 | 1.78436410718814+13.4959699421067j | 1.7844 | 13.496
249 | 350.1562 | 341.5411 | 3.5026 | 333.8575 | -57.9298 | 7.6836 | 23.2586 | 2.26 | 13.0245 | 1.2426 | -0.4105 | -25.1291 | 8.7122 | -16.4169 | 358.9865 | -1.0286 | 357.9579 | 1196.2726 | 284.3682 | 249 | -34.6712 | 1.35259242222152+13.3242072498075j | 1.3526 | 13.3242
250 | 351.5625 | 336.3805 | 3.2467 | 335.1786 | -49.719 | 1.2019 | 24.4654 | 1.9396 | 13.076 | 1.3071 | -0.064213 | -25.2285 | 1.3628 | -23.8657 | 360.4071 | -0.1609 | 360.2462 | 1092.137 | 240.8569 | 250 | -25.2537 | 0.985196069297548+13.1228826587699j | 0.9852 | 13.1229
251 | 352.9688 | 330.9309 | 2.895 | 336.2978 | -41.4784 | -5.3669 | 23.8997 | 1.6182 | 13.1197 | 1.2769 | 0.28673 | -25.3127 | -6.0853 | -31.3981 | 361.6105 | 0.71846 | 362.329 | 958.0531 | 189.2712 | 251 | -17.5787 | 0.685778810769791+12.9102845810603j | 0.68578 | 12.9103
252 | 354.375 | 325.6676 | 2.4498 | 337.2144 | -33.2127 | -11.5468 | 21.6026 | 1.2957 | 13.1554 | 1.1541 | 0.6169 | -25.3817 | -13.0926 | -38.4743 | 362.5962 | 1.5458 | 364.1419 | 797.8325 | 134.2885 | 252 | -11.6102 | 0.452935526596699+12.704952278435j | 0.45294 | 12.705
253 | 355.7812 | 321.0377 | 1.9203 | 337.928 | -24.9271 | -16.8902 | 17.7404 | 0.97246 | 13.1833 | 0.9478 | 0.90238 | -25.4354 | -19.1513 | -44.5867 | 363.3634 | 2.2611 | 365.6245 | 616.4738 | 81.9323 | 253 | -7.1867 | 0.280367925220719+12.5243308427429j | 0.28037 | 12.5243
254 | 357.1875 | 317.428 | 1.3214 | 338.4379 | -16.6264 | -21.01 | 12.5929 | 0.64863 | 13.2031 | 0.67279 | 1.1225 | -25.4738 | -23.8226 | -49.2964 | 363.9117 | 2.8126 | 366.7243 | 419.4551 | 38.6109 | 254 | -4.0335 | 0.157354796476097+12.3835057886138j | 0.15735 | 12.3835
255 | 358.5938 | 315.1364 | 0.67345 | 338.744 | -8.3157 | -23.6076 | 6.5331 | 0.32441 | 13.2151 | 0.34904 | 1.2613 | -25.4969 | -26.7679 | -52.2648 | 364.2409 | 3.1603 | 367.4012 | 212.2287 | 9.9999 | 255 | -1.7826 | 0.06954272929886+12.2941089354287j | 0.069543 | 12.2941
|  | Sqr V | Sqr I | Sqr V1 |  | Sqr Vn |  | Sqr I1 |  | Sqr In |  | Sqr V1L | Sqr VnL | Sqr VL | Sqr V1c | Sqr Vnc | Sqr Vc
0 |  | 98816.6667 | 2.5706e-32 | 114816.6667 |  | 600 |  | 0 |  | 2.5706e-32 |  | 650.4818 | 771.3951 | 2838.6032 | 132751.3778 | 10.7525 | 135151.6166 | [5 empty] | 1.3706e-32
1 |  | 99310.9702 | 0.45354 | 114747.5158 |  | 557.3186 |  | 0.10524 |  | 0.12183 |  | 650.09 | 716.5214 | 2731.6071 | 132671.4254 | 9.9876 | 134983.6491 | [5 empty] | 0.0048362
2 |  | 100760.5046 | 1.7461 | 114540.2299 |  | 441.419 |  | 0.42072 |  | 0.45265 |  | 648.9156 | 567.5141 | 2430.1328 | 132431.7607 | 7.9106 | 134486.7333 | [5 empty] | 0.024761
3 |  | 103065.2292 | 3.6874 | 114195.3081 |  | 285.2797 |  | 0.94567 |  | 0.89832 |  | 646.9615 | 366.7723 | 1987.9771 | 132032.9612 | 5.1125 | 133681.2569 | [5 empty] | 0.078606
4 |  | 106059.4051 | 6.0017 | 113713.5816 |  | 133.3289 |  | 1.6788 |  | 1.332 |  | 644.2323 | 171.4155 | 1480.2722 | 131475.9876 | 2.3894 | 132599.349 | [5 empty] | 0.20515
5 |  | 109515.286 | 8.3812 | 113096.2109 |  | 28.8032 |  | 2.6184 |  | 1.6304 |  | 640.7347 | 37.0311 | 985.8379 | 130762.1816 | 0.51618 | 131282.2999 | [5 empty] | 0.47029
6 |  | 113151.8351 | 10.5413 | 112344.6831 |  | 1.4446 |  | 3.7622 |  | 1.7085 |  | 636.477 | 1.8572 | 569.5712 | 129893.2629 | 0.025888 | 129777.3113 | [5 empty] | 0.97061
7 |  | 116650.3025 | 12.268 | 111460.8089 |  | 59.0377 |  | 5.1074 |  | 1.5441 |  | 631.4695 | 75.9024 | 269.5133 | 128871.3249 | 1.058 | 128133.8796 | [5 empty] | 1.8295
8 |  | 119677.1712 | 13.4471 | 110446.7175 |  | 185.195 |  | 6.6508 |  | 1.184 |  | 625.7243 | 238.0975 | 91.8545 | 127698.8293 | 3.3189 | 126400.1288 | [5 empty] | 3.184
9 |  | 121913.1219 | 14.0708 | 109304.852 |  | 344.0191 |  | 8.3886 |  | 0.73066 |  | 619.2551 | 442.2911 | 14.8542 | 126378.601 | 6.1651 | 124619.3891 | [5 empty] | 5.1626
10 |  | 123084.7858 | 14.2242 | 108037.9633 |  | 490.318 |  | 10.3168 |  | 0.31307 |  | 612.0777 | 630.3815 | 0.13483 | 124913.8204 | 8.7869 | 122827.2719 | [5 empty] | 7.8591
11 |  | 122994.7109 | 14.0582 | 106649.1033 |  | 582.4632 |  | 12.4305 |  | 0.050056 |  | 604.2093 | 748.8488 | 7.7531 | 123308.0163 | 10.4382 | 121049.4294 | [5 empty] | 11.3052
12 |  | 121544.5715 | 13.7568 | 105141.618 |  | 594.2356 |  | 14.7248 |  | 0.016454 |  | 595.6688 | 763.984 | 10.4583 | 121565.0572 | 10.6492 | 119300.1212 | [5 empty] | 15.4524
13 |  | 118747.4134 | 13.51 | 103519.139 |  | 522.2853 |  | 17.1941 |  | 0.22182 |  | 586.4768 | 671.4806 | 2.8753 | 119689.1421 | 9.3598 | 117581.649 | [5 empty] | 20.1645
14 |  | 114726.4982 | 13.4968 | 101785.5751 |  | 387.0854 |  | 19.8325 |  | 0.60773 |  | 576.6555 | 497.6596 | 2.9083 | 117684.7903 | 6.9369 | 115884.6656 | [5 empty] | 25.2267
15 |  | 109700.7188 | 13.8815 | 99945.1025 |  | 227.1059 |  | 22.6336 |  | 1.0644 |  | 566.2285 | 291.9807 | 44.9988 | 115556.8303 | 4.0699 | 114189.3192 | [5 empty] | 30.3691
16 |  | 103959.0094 | 14.8199 | 98002.1551 |  | 87.868 |  | 25.5906 |  | 1.4618 |  | 555.2209 | 112.9682 | 167.3007 | 113310.3886 | 1.5747 | 112467.1523 | [5 empty] | 35.3023
17 |  | 97828.0942 | 16.4681 | 95961.4137 |  | 8.9906 |  | 28.6965 |  | 1.6869 |  | 543.6593 | 11.5589 | 396.6737 | 110950.8772 | 0.16112 | 110683.6332 | [5 empty] | 39.7571
18 |  | 91638.8422 | 18.9867 | 93827.7945 |  | 12.9179 |  | 31.9438 |  | 1.6757 |  | 531.5715 | 16.608 | 736.098 | 108483.9802 | 0.2315 | 108801.1598 | [5 empty] | 43.5222
19 |  | 85696.2448 | 22.5345 | 91606.4376 |  | 98.5323 |  | 35.3245 |  | 1.4314 |  | 518.9866 | 126.6789 | 1158.48 | 105915.6406 | 1.7658 | 106782.3321 | [5 empty] | 46.4723
20 |  | 80256.7176 | 27.2465 | 89302.6945 |  | 241.4729 |  | 38.8307 |  | 1.0234 |  | 505.935 | 310.4517 | 1609.0238 | 103252.0459 | 4.3274 | 104593.2548 | [5 empty] | 48.5825
21 |  | 75514.4415 | 33.202 | 86922.115 |  | 401.067 |  | 42.4538 |  | 0.56782 |  | 492.4481 | 515.6351 | 2015.8998 | 100499.6127 | 7.1875 | 102206.6088 | [5 empty] | 49.9269
22 |  | 71596.3554 | 40.3871 | 84470.4343 |  | 531.9031 |  | 46.1851 |  | 0.19437 |  | 478.5584 | 683.8458 | 2306.5372 | 97664.9721 | 9.5322 | 99604.2277 | [5 empty] | 50.6644
23 |  | 68563.7426 | 48.6632 | 81953.5587 |  | 596.753 |  | 50.0156 |  | 0.0092682 |  | 464.2993 | 767.2205 | 2425.203 | 94754.9528 | 10.6943 | 96778.9432 | [5 empty] | 51.0149
24 |  | 66417.5288 | 57.7513 | 79377.5514 |  | 577.1639 |  | 53.9361 |  | 0.065182 |  | 449.7052 | 742.0356 | 2347.0715 | 91776.5654 | 10.3433 | 93735.5183 | [5 empty] | 51.2326
25 |  | 65104.5702 | 67.2407 | 76748.6183 |  | 478.7098 |  | 57.9372 |  | 0.3462 |  | 434.8112 | 615.4573 | 2084.8849 | 88736.985 | 8.5789 | 90490.5738 | [5 empty] | 51.5812
26 |  | 64523.2151 | 76.6227 | 74073.0928 |  | 329.4051 |  | 62.0092 |  | 0.77237 |  | 419.6533 | 423.5025 | 1686.3029 | 85643.5343 | 5.9032 | 87071.5105 | [5 empty] | 52.3142
27 |  | 64527.8805 | 85.3484 | 71357.4205 |  | 171.7335 |  | 66.1423 |  | 1.2224 |  | 404.268 | 220.7906 | 1222.582 | 82503.6657 | 3.0776 | 83514.5413 | [5 empty] | 53.6622
28 |  | 64933.7774 | 92.8989 | 68608.1436 |  | 50.5591 |  | 70.3265 |  | 1.5683 |  | 388.6922 | 65.0018 | 771.5976 | 79324.9434 | 0.90606 | 79862.0337 | [5 empty] | 55.8254
29 |  | 65523.7716 | 98.8555 | 65831.8853 |  | 0.36136 |  | 74.5518 |  | 1.7116 |  | 372.9636 | 0.46459 | 399.755 | 76115.0252 | 0.0064759 | 76159.4351 | [5 empty] | 58.9675
30 |  | 66059.3625 | 102.9582 | 63035.334 |  | 35.4236 |  | 78.808 |  | 1.6115 |  | 357.1201 | 45.5427 | 147.6004 | 72881.6441 | 0.63482 | 72452.0843 | [5 empty] | 63.2093
31 |  | 66296.8652 | 105.1392 | 60225.2267 |  | 145.7692 |  | 83.0848 |  | 1.2965 |  | 341.1997 | 187.4094 | 22.866 | 69632.5896 | 2.6123 | 68782.2029 | [5 empty] | 68.6186
32 |  | 66008.3333 | 105.5276 | 57408.3333 |  | 300 |  | 87.3719 |  | 0.8563 |  | 325.2409 | 385.6975 | 2.5752 | 66375.6889 | 5.3763 | 65186.322 | [5 empty] | 75.1964
33 |  | 65005.011 | 104.4262 | 54591.4399 |  | 454.2308 |  | 91.659 |  | 0.41608 |  | 309.2821 | 583.9857 | 43.2882 | 63118.7882 | 8.1402 | 61693.3316 | [5 empty] | 82.8621
34 |  | 63159.6997 | 102.266 | 51781.3327 |  | 564.5764 |  | 95.9359 |  | 0.10111 |  | 293.3617 | 725.8524 | 96.3115 | 59869.7337 | 10.1177 | 58323.2608 | [5 empty] | 91.4413
35 |  | 60423.8236 | 99.5501 | 48984.7813 |  | 599.6386 |  | 100.192 |  | 0.0010315 |  | 277.5181 | 770.9305 | 123.3601 | 56636.3526 | 10.746 | 55086.8212 | [5 empty] | 100.6621
36 |  | 56835.4343 | 96.7979 | 46208.5231 |  | 549.4409 |  | 104.4173 |  | 0.14431 |  | 261.7895 | 706.3933 | 108.1215 | 53426.4344 | 9.8465 | 51985.6798 | [5 empty] | 110.1634
37 |  | 52515.8707 | 94.4993 | 43459.2462 |  | 428.2665 |  | 108.6016 |  | 0.49019 |  | 246.2138 | 550.6045 | 60.4314 | 50247.7121 | 7.6749 | 49013.3784 | [5 empty] | 119.5184
38 |  | 47654.9522 | 93.0839 | 40743.5738 |  | 270.5949 |  | 112.7346 |  | 0.94024 |  | 230.8284 | 347.8926 | 11.9636 | 47107.8435 | 4.8493 | 46156.7855 | [5 empty] | 128.2716
39 |  | 42486.9107 | 92.906 | 38068.0483 |  | 121.2902 |  | 116.8066 |  | 1.3664 |  | 215.6705 | 155.9378 | 4.8322 | 44014.3928 | 2.1736 | 43397.9526 | [5 empty] | 135.9853
40 |  | 37261.1653 | 94.2401 | 35439.1153 |  | 22.8361 |  | 120.8077 |  | 1.6474 |  | 200.7766 | 29.3595 | 76.5822 | 40974.8124 | 0.40924 | 40716.2339 | [5 empty] | 142.2889
41 |  | 32213.0311 | 97.2799 | 32863.108 |  | 3.247 |  | 124.7282 |  | 1.7033 |  | 186.1825 | 4.1746 | 246.115 | 37996.425 | 0.05819 | 38090.5259 | [5 empty] | 146.9231
42 |  | 27539.2756 | 102.1354 | 30346.2323 |  | 68.0969 |  | 128.5587 |  | 1.5182 |  | 171.9234 | 87.5493 | 504.844 | 35086.4058 | 1.2204 | 35501.4756 | [5 empty] | 149.7713
43 |  | 23382.1587 | 108.8223 | 27894.5516 |  | 198.933 |  | 132.29 |  | 1.1448 |  | 158.0336 | 255.76 | 815.8815 | 32251.7651 | 3.5651 | 32933.5017 | [5 empty] | 150.8726
44 |  | 19823.5489 | 117.2449 | 25513.9722 |  | 358.5271 |  | 135.9131 |  | 0.68925 |  | 144.5467 | 460.9434 | 1121.7376 | 29499.332 | 6.4251 | 30376.473 | [5 empty] | 150.4156
45 |  | 16888.4483 | 127.1768 | 23210.2291 |  | 501.4677 |  | 139.4193 |  | 0.28125 |  | 131.4951 | 644.7162 | 1358.5412 | 26835.7372 | 8.9867 | 27826.8961 | [5 empty] | 148.7142
46 |  | 14555.3586 | 138.2477 | 20988.8722 |  | 587.0821 |  | 142.8001 |  | 0.036872 |  | 118.9102 | 754.7871 | 1472.8698 | 24267.3976 | 10.521 | 25288.498 | [5 empty] | 146.1708
47 |  | 12769.8468 | 149.9449 | 18855.253 |  | 591.0094 |  | 146.0473 |  | 0.025662 |  | 106.8225 | 759.8362 | 1436.4571 | 21800.5006 | 10.5914 | 22772.1284 | [5 empty] | 143.2337
48 |  | 11457.6573 | 161.6365 | 16814.5115 |  | 512.132 |  | 149.1532 |  | 0.25081 |  | 95.2608 | 658.4269 | 1254.5762 | 19440.9892 | 9.1778 | 20294.978 | [5 empty] | 140.3547
49 |  | 10534.6736 | 172.6184 | 14871.5641 |  | 372.8941 |  | 152.1102 |  | 0.64824 |  | 84.2533 | 479.4144 | 965.6241 | 17194.5475 | 6.6826 | 17879.1798 | [5 empty] | 137.9541
50 |  | 9912.6343 | 182.1816 | 13031.0916 |  | 212.9146 |  | 154.9113 |  | 1.1049 |  | 73.8263 | 273.7355 | 631.8775 | 15066.5875 | 3.8156 | 15549.9373 | [5 empty] | 136.3943
51 |  | 9501.2268 | 189.6916 | 11297.5276 |  | 77.7147 |  | 157.5497 |  | 1.4908 |  | 64.005 | 99.9145 | 323.8573 | 13062.2357 | 1.3927 | 13333.3835 | [5 empty] | 135.963
52 |  | 9208.4954 | 194.6646 | 9675.0487 |  | 5.7644 |  | 160.019 |  | 1.6962 |  | 54.813 | 7.4111 | 102.534 | 11186.3206 | 0.1033 | 11254.4116 | [5 empty] | 136.8635
53 |  | 8942.0223 | 196.8303 | 8167.5634 |  | 17.5368 |  | 162.3133 |  | 1.6626 |  | 46.2725 | 22.5463 | 4.2193 | 9443.3615 | 0.31427 | 9334.7207 | [5 empty] | 139.2092
54 |  | 8612.9165 | 196.1661 | 6778.7034 |  | 109.682 |  | 164.4271 |  | 1.3995 |  | 38.404 | 141.0136 | 32.2376 | 7837.5574 | 1.9656 | 7591.2855 | [5 empty] | 143.0192
55 |  | 8143.4378 | 192.899 | 5511.8147 |  | 255.9809 |  | 166.3552 |  | 0.98195 |  | 31.2266 | 329.104 | 157.5815 | 6372.7768 | 4.5874 | 6035.4025 | [5 empty] | 148.2133
56 |  | 7477.468 | 187.4743 | 4369.9492 |  | 414.805 |  | 168.093 |  | 0.52861 |  | 24.7575 | 533.2976 | 328.2455 | 5052.5485 | 7.4337 | 4672.3796 | [5 empty] | 154.6086
57 |  | 6591.55 | 180.4981 | 3355.8578 |  | 540.9623 |  | 169.6364 |  | 0.16851 |  | 19.0123 | 695.4927 | 484.5233 | 3880.0529 | 9.6945 | 3501.8547 | [5 empty] | 161.918
58 |  | 5503.3309 | 172.665 | 2471.9836 |  | 598.5554 |  | 170.9816 |  | 0.0041233 |  | 14.0048 | 769.5378 | 575.9161 | 2858.1149 | 10.7266 | 2518.6534 | [5 empty] | 169.7576
59 |  | 4274.2961 | 164.684 | 1720.4558 |  | 571.1968 |  | 172.1254 |  | 0.082214 |  | 9.7471 | 734.364 | 574.9024 | 1989.1962 | 10.2363 | 1714.041 | [5 empty] | 177.663
60 |  | 3004.7165 | 157.2144 | 1103.085 |  | 466.6711 |  | 173.065 |  | 0.38057 |  | 6.2494 | 599.9796 | 483.7624 | 1275.3903 | 8.3631 | 1077.1981 | [5 empty] | 185.12
61 |  | 1820.5089 | 150.8199 | 621.3585 |  | 314.7203 |  | 173.7982 |  | 0.81429 |  | 3.5202 | 404.6228 | 332.6614 | 718.4166 | 5.6401 | 596.7474 | [5 empty] | 191.6058
62 |  | 853.7665 | 145.9425 | 276.4368 |  | 158.581 |  | 174.3231 |  | 1.26 |  | 1.5661 | 203.881 | 169.709 | 319.6171 | 2.8419 | 262.1822 | [5 empty] | 196.6386
63 |  | 220.4869 | 142.894 | 69.1509 |  | 42.6814 |  | 174.6386 |  | 1.5908 |  | 0.39177 | 54.8737 | 45.9924 | 79.9524 | 0.76489 | 65.077 | [5 empty] | 199.8284
64 |  | 1.0552e-29 | 141.8577 | 4.3085e-28 |  | 5.7625e-28 |  | 174.7438 |  | 1.7126 |  | 2.4409e-30 | 7.4086e-28 | 8.2835e-28 | 4.9815e-28 | 1.0327e-29 | 6.5192e-28 | [5 empty] | 200.9211
65 |  | 220.4869 | 142.894 | 69.1509 |  | 42.6814 |  | 174.6386 |  | 1.5908 |  | 0.39177 | 54.8737 | 45.9924 | 79.9524 | 0.76489 | 65.077 | [5 empty] | 199.8284
66 |  | 853.7665 | 145.9425 | 276.4368 |  | 158.581 |  | 174.3231 |  | 1.26 |  | 1.5661 | 203.881 | 169.709 | 319.6171 | 2.8419 | 262.1822 | [5 empty] | 196.6386
67 |  | 1820.5089 | 150.8199 | 621.3585 |  | 314.7203 |  | 173.7982 |  | 0.81429 |  | 3.5202 | 404.6228 | 332.6614 | 718.4166 | 5.6401 | 596.7474 | [5 empty] | 191.6058
68 |  | 3004.7165 | 157.2144 | 1103.085 |  | 466.6711 |  | 173.065 |  | 0.38057 |  | 6.2494 | 599.9796 | 483.7624 | 1275.3903 | 8.3631 | 1077.1981 | [5 empty] | 185.12
69 |  | 4274.2961 | 164.684 | 1720.4558 |  | 571.1968 |  | 172.1254 |  | 0.082214 |  | 9.7471 | 734.364 | 574.9024 | 1989.1962 | 10.2363 | 1714.041 | [5 empty] | 177.663
70 |  | 5503.3309 | 172.665 | 2471.9836 |  | 598.5554 |  | 170.9816 |  | 0.0041233 |  | 14.0048 | 769.5378 | 575.9161 | 2858.1149 | 10.7266 | 2518.6534 | [5 empty] | 169.7576
71 |  | 6591.55 | 180.4981 | 3355.8578 |  | 540.9623 |  | 169.6364 |  | 0.16851 |  | 19.0123 | 695.4927 | 484.5233 | 3880.0529 | 9.6945 | 3501.8547 | [5 empty] | 161.918
72 |  | 7477.468 | 187.4743 | 4369.9492 |  | 414.805 |  | 168.093 |  | 0.52861 |  | 24.7575 | 533.2976 | 328.2455 | 5052.5485 | 7.4337 | 4672.3796 | [5 empty] | 154.6086
73 |  | 8143.4378 | 192.899 | 5511.8147 |  | 255.9809 |  | 166.3552 |  | 0.98195 |  | 31.2266 | 329.104 | 157.5815 | 6372.7768 | 4.5874 | 6035.4025 | [5 empty] | 148.2133
74 |  | 8612.9165 | 196.1661 | 6778.7034 |  | 109.682 |  | 164.4271 |  | 1.3995 |  | 38.404 | 141.0136 | 32.2376 | 7837.5574 | 1.9656 | 7591.2855 | [5 empty] | 143.0192
75 |  | 8942.0223 | 196.8303 | 8167.5634 |  | 17.5368 |  | 162.3133 |  | 1.6626 |  | 46.2725 | 22.5463 | 4.2193 | 9443.3615 | 0.31427 | 9334.7207 | [5 empty] | 139.2092
76 |  | 9208.4954 | 194.6646 | 9675.0487 |  | 5.7644 |  | 160.019 |  | 1.6962 |  | 54.813 | 7.4111 | 102.534 | 11186.3206 | 0.1033 | 11254.4116 | [5 empty] | 136.8635
77 |  | 9501.2268 | 189.6916 | 11297.5276 |  | 77.7147 |  | 157.5497 |  | 1.4908 |  | 64.005 | 99.9145 | 323.8573 | 13062.2357 | 1.3927 | 13333.3835 | [5 empty] | 135.963
78 |  | 9912.6343 | 182.1816 | 13031.0916 |  | 212.9146 |  | 154.9113 |  | 1.1049 |  | 73.8263 | 273.7355 | 631.8775 | 15066.5875 | 3.8156 | 15549.9373 | [5 empty] | 136.3943
79 |  | 10534.6736 | 172.6184 | 14871.5641 |  | 372.8941 |  | 152.1102 |  | 0.64824 |  | 84.2533 | 479.4144 | 965.6241 | 17194.5475 | 6.6826 | 17879.1798 | [5 empty] | 137.9541
80 |  | 11457.6573 | 161.6365 | 16814.5115 |  | 512.132 |  | 149.1532 |  | 0.25081 |  | 95.2608 | 658.4269 | 1254.5762 | 19440.9892 | 9.1778 | 20294.978 | [5 empty] | 140.3547
81 |  | 12769.8468 | 149.9449 | 18855.253 |  | 591.0094 |  | 146.0473 |  | 0.025662 |  | 106.8225 | 759.8362 | 1436.4571 | 21800.5006 | 10.5914 | 22772.1284 | [5 empty] | 143.2337
82 |  | 14555.3586 | 138.2477 | 20988.8722 |  | 587.0821 |  | 142.8001 |  | 0.036872 |  | 118.9102 | 754.7871 | 1472.8698 | 24267.3976 | 10.521 | 25288.498 | [5 empty] | 146.1708
83 |  | 16888.4483 | 127.1768 | 23210.2291 |  | 501.4677 |  | 139.4193 |  | 0.28125 |  | 131.4951 | 644.7162 | 1358.5412 | 26835.7372 | 8.9867 | 27826.8961 | [5 empty] | 148.7142
84 |  | 19823.5489 | 117.2449 | 25513.9722 |  | 358.5271 |  | 135.9131 |  | 0.68925 |  | 144.5467 | 460.9434 | 1121.7376 | 29499.332 | 6.4251 | 30376.473 | [5 empty] | 150.4156
85 |  | 23382.1587 | 108.8223 | 27894.5516 |  | 198.933 |  | 132.29 |  | 1.1448 |  | 158.0336 | 255.76 | 815.8815 | 32251.7651 | 3.5651 | 32933.5017 | [5 empty] | 150.8726
86 |  | 27539.2756 | 102.1354 | 30346.2323 |  | 68.0969 |  | 128.5587 |  | 1.5182 |  | 171.9234 | 87.5493 | 504.844 | 35086.4058 | 1.2204 | 35501.4756 | [5 empty] | 149.7713
87 |  | 32213.0311 | 97.2799 | 32863.108 |  | 3.247 |  | 124.7282 |  | 1.7033 |  | 186.1825 | 4.1746 | 246.115 | 37996.425 | 0.05819 | 38090.5259 | [5 empty] | 146.9231
88 |  | 37261.1653 | 94.2401 | 35439.1153 |  | 22.8361 |  | 120.8077 |  | 1.6474 |  | 200.7766 | 29.3595 | 76.5822 | 40974.8124 | 0.40924 | 40716.2339 | [5 empty] | 142.2889
89 |  | 42486.9107 | 92.906 | 38068.0483 |  | 121.2902 |  | 116.8066 |  | 1.3664 |  | 215.6705 | 155.9378 | 4.8322 | 44014.3928 | 2.1736 | 43397.9526 | [5 empty] | 135.9853
90 |  | 47654.9522 | 93.0839 | 40743.5738 |  | 270.5949 |  | 112.7346 |  | 0.94024 |  | 230.8284 | 347.8926 | 11.9636 | 47107.8435 | 4.8493 | 46156.7855 | [5 empty] | 128.2716
91 |  | 52515.8707 | 94.4993 | 43459.2462 |  | 428.2665 |  | 108.6016 |  | 0.49019 |  | 246.2138 | 550.6045 | 60.4314 | 50247.7121 | 7.6749 | 49013.3784 | [5 empty] | 119.5184
92 |  | 56835.4343 | 96.7979 | 46208.5231 |  | 549.4409 |  | 104.4173 |  | 0.14431 |  | 261.7895 | 706.3933 | 108.1215 | 53426.4344 | 9.8465 | 51985.6798 | [5 empty] | 110.1634
93 |  | 60423.8236 | 99.5501 | 48984.7813 |  | 599.6386 |  | 100.192 |  | 0.0010315 |  | 277.5181 | 770.9305 | 123.3601 | 56636.3526 | 10.746 | 55086.8212 | [5 empty] | 100.6621
94 |  | 63159.6997 | 102.266 | 51781.3327 |  | 564.5764 |  | 95.9359 |  | 0.10111 |  | 293.3617 | 725.8524 | 96.3115 | 59869.7337 | 10.1177 | 58323.2608 | [5 empty] | 91.4413
95 |  | 65005.011 | 104.4262 | 54591.4399 |  | 454.2308 |  | 91.659 |  | 0.41608 |  | 309.2821 | 583.9857 | 43.2882 | 63118.7882 | 8.1402 | 61693.3316 | [5 empty] | 82.8621
96 |  | 66008.3333 | 105.5276 | 57408.3333 |  | 300 |  | 87.3719 |  | 0.8563 |  | 325.2409 | 385.6975 | 2.5752 | 66375.6889 | 5.3763 | 65186.322 | [5 empty] | 75.1964
97 |  | 66296.8652 | 105.1392 | 60225.2267 |  | 145.7692 |  | 83.0848 |  | 1.2965 |  | 341.1997 | 187.4094 | 22.866 | 69632.5896 | 2.6123 | 68782.2029 | [5 empty] | 68.6186
98 |  | 66059.3625 | 102.9582 | 63035.334 |  | 35.4236 |  | 78.808 |  | 1.6115 |  | 357.1201 | 45.5427 | 147.6004 | 72881.6441 | 0.63482 | 72452.0843 | [5 empty] | 63.2093
99 |  | 65523.7716 | 98.8555 | 65831.8853 |  | 0.36136 |  | 74.5518 |  | 1.7116 |  | 372.9636 | 0.46459 | 399.755 | 76115.0252 | 0.0064759 | 76159.4351 | [5 empty] | 58.9675
100 |  | 64933.7774 | 92.8989 | 68608.1436 |  | 50.5591 |  | 70.3265 |  | 1.5683 |  | 388.6922 | 65.0018 | 771.5976 | 79324.9434 | 0.90606 | 79862.0337 | [5 empty] | 55.8254
101 |  | 64527.8805 | 85.3484 | 71357.4205 |  | 171.7335 |  | 66.1423 |  | 1.2224 |  | 404.268 | 220.7906 | 1222.582 | 82503.6657 | 3.0776 | 83514.5413 | [5 empty] | 53.6622
102 |  | 64523.2151 | 76.6227 | 74073.0928 |  | 329.4051 |  | 62.0092 |  | 0.77237 |  | 419.6533 | 423.5025 | 1686.3029 | 85643.5343 | 5.9032 | 87071.5105 | [5 empty] | 52.3142
103 |  | 65104.5702 | 67.2407 | 76748.6183 |  | 478.7098 |  | 57.9372 |  | 0.3462 |  | 434.8112 | 615.4573 | 2084.8849 | 88736.985 | 8.5789 | 90490.5738 | [5 empty] | 51.5812
104 |  | 66417.5288 | 57.7513 | 79377.5514 |  | 577.1639 |  | 53.9361 |  | 0.065182 |  | 449.7052 | 742.0356 | 2347.0715 | 91776.5654 | 10.3433 | 93735.5183 | [5 empty] | 51.2326
105 |  | 68563.7426 | 48.6632 | 81953.5587 |  | 596.753 |  | 50.0156 |  | 0.0092682 |  | 464.2993 | 767.2205 | 2425.203 | 94754.9528 | 10.6943 | 96778.9432 | [5 empty] | 51.0149
106 |  | 71596.3554 | 40.3871 | 84470.4343 |  | 531.9031 |  | 46.1851 |  | 0.19437 |  | 478.5584 | 683.8458 | 2306.5372 | 97664.9721 | 9.5322 | 99604.2277 | [5 empty] | 50.6644
107 |  | 75514.4415 | 33.202 | 86922.115 |  | 401.067 |  | 42.4538 |  | 0.56782 |  | 492.4481 | 515.6351 | 2015.8998 | 100499.6127 | 7.1875 | 102206.6088 | [5 empty] | 49.9269
108 |  | 80256.7176 | 27.2465 | 89302.6945 |  | 241.4729 |  | 38.8307 |  | 1.0234 |  | 505.935 | 310.4517 | 1609.0238 | 103252.0459 | 4.3274 | 104593.2548 | [5 empty] | 48.5825
109 |  | 85696.2448 | 22.5345 | 91606.4376 |  | 98.5323 |  | 35.3245 |  | 1.4314 |  | 518.9866 | 126.6789 | 1158.48 | 105915.6406 | 1.7658 | 106782.3321 | [5 empty] | 46.4723
110 |  | 91638.8422 | 18.9867 | 93827.7945 |  | 12.9179 |  | 31.9438 |  | 1.6757 |  | 531.5715 | 16.608 | 736.098 | 108483.9802 | 0.2315 | 108801.1598 | [5 empty] | 43.5222
111 |  | 97828.0942 | 16.4681 | 95961.4137 |  | 8.9906 |  | 28.6965 |  | 1.6869 |  | 543.6593 | 11.5589 | 396.6737 | 110950.8772 | 0.16112 | 110683.6332 | [5 empty] | 39.7571
112 |  | 103959.0094 | 14.8199 | 98002.1551 |  | 87.868 |  | 25.5906 |  | 1.4618 |  | 555.2209 | 112.9682 | 167.3007 | 113310.3886 | 1.5747 | 112467.1523 | [5 empty] | 35.3023
113 |  | 109700.7188 | 13.8815 | 99945.1025 |  | 227.1059 |  | 22.6336 |  | 1.0644 |  | 566.2285 | 291.9807 | 44.9988 | 115556.8303 | 4.0699 | 114189.3192 | [5 empty] | 30.3691
114 |  | 114726.4982 | 13.4968 | 101785.5751 |  | 387.0854 |  | 19.8325 |  | 0.60773 |  | 576.6555 | 497.6596 | 2.9083 | 117684.7903 | 6.9369 | 115884.6656 | [5 empty] | 25.2267
115 |  | 118747.4134 | 13.51 | 103519.139 |  | 522.2853 |  | 17.1941 |  | 0.22182 |  | 586.4768 | 671.4806 | 2.8753 | 119689.1421 | 9.3598 | 117581.649 | [5 empty] | 20.1645
116 |  | 121544.5715 | 13.7568 | 105141.618 |  | 594.2356 |  | 14.7248 |  | 0.016454 |  | 595.6688 | 763.984 | 10.4583 | 121565.0572 | 10.6492 | 119300.1212 | [5 empty] | 15.4524
117 |  | 122994.7109 | 14.0582 | 106649.1033 |  | 582.4632 |  | 12.4305 |  | 0.050056 |  | 604.2093 | 748.8488 | 7.7531 | 123308.0163 | 10.4382 | 121049.4294 | [5 empty] | 11.3052
118 |  | 123084.7858 | 14.2242 | 108037.9633 |  | 490.318 |  | 10.3168 |  | 0.31307 |  | 612.0777 | 630.3815 | 0.13483 | 124913.8204 | 8.7869 | 122827.2719 | [5 empty] | 7.8591
119 |  | 121913.1219 | 14.0708 | 109304.852 |  | 344.0191 |  | 8.3886 |  | 0.73066 |  | 619.2551 | 442.2911 | 14.8542 | 126378.601 | 6.1651 | 124619.3891 | [5 empty] | 5.1626
120 |  | 119677.1712 | 13.4471 | 110446.7175 |  | 185.195 |  | 6.6508 |  | 1.184 |  | 625.7243 | 238.0975 | 91.8545 | 127698.8293 | 3.3189 | 126400.1288 | [5 empty] | 3.184
121 |  | 116650.3025 | 12.268 | 111460.8089 |  | 59.0377 |  | 5.1074 |  | 1.5441 |  | 631.4695 | 75.9024 | 269.5133 | 128871.3249 | 1.058 | 128133.8796 | [5 empty] | 1.8295
122 |  | 113151.8351 | 10.5413 | 112344.6831 |  | 1.4446 |  | 3.7622 |  | 1.7085 |  | 636.477 | 1.8572 | 569.5712 | 129893.2629 | 0.025888 | 129777.3113 | [5 empty] | 0.97061
123 |  | 109515.286 | 8.3812 | 113096.2109 |  | 28.8032 |  | 2.6184 |  | 1.6304 |  | 640.7347 | 37.0311 | 985.8379 | 130762.1816 | 0.51618 | 131282.2999 | [5 empty] | 0.47029
124 |  | 106059.4051 | 6.0017 | 113713.5816 |  | 133.3289 |  | 1.6788 |  | 1.332 |  | 644.2323 | 171.4155 | 1480.2722 | 131475.9876 | 2.3894 | 132599.349 | [5 empty] | 0.20515
125 |  | 103065.2292 | 3.6874 | 114195.3081 |  | 285.2797 |  | 0.94567 |  | 0.89832 |  | 646.9615 | 366.7723 | 1987.9771 | 132032.9612 | 5.1125 | 133681.2569 | [5 empty] | 0.078606
126 |  | 100760.5046 | 1.7461 | 114540.2299 |  | 441.419 |  | 0.42072 |  | 0.45265 |  | 648.9156 | 567.5141 | 2430.1328 | 132431.7607 | 7.9106 | 134486.7333 | [5 empty] | 0.024761
127 |  | 99310.9702 | 0.45354 | 114747.5158 |  | 557.3186 |  | 0.10524 |  | 0.12183 |  | 650.09 | 716.5214 | 2731.6071 | 132671.4254 | 9.9876 | 134983.6491 | [5 empty] | 0.0048362
128 |  | 98816.6667 | 1.2556e-29 | 114816.6667 |  | 600 |  | 2.6229e-30 |  | 3.7017e-30 |  | 650.4818 | 771.3951 | 2838.6032 | 132751.3778 | 10.7525 | 135151.6166 | [5 empty] | 4.6069e-32
129 |  | 99310.9702 | 0.45354 | 114747.5158 |  | 557.3186 |  | 0.10524 |  | 0.12183 |  | 650.09 | 716.5214 | 2731.6071 | 132671.4254 | 9.9876 | 134983.6491 | [5 empty] | 0.0048362
130 |  | 100760.5046 | 1.7461 | 114540.2299 |  | 441.419 |  | 0.42072 |  | 0.45265 |  | 648.9156 | 567.5141 | 2430.1328 | 132431.7607 | 7.9106 | 134486.7333 | [5 empty] | 0.024761
131 |  | 103065.2292 | 3.6874 | 114195.3081 |  | 285.2797 |  | 0.94567 |  | 0.89832 |  | 646.9615 | 366.7723 | 1987.9771 | 132032.9612 | 5.1125 | 133681.2569 | [5 empty] | 0.078606
132 |  | 106059.4051 | 6.0017 | 113713.5816 |  | 133.3289 |  | 1.6788 |  | 1.332 |  | 644.2323 | 171.4155 | 1480.2722 | 131475.9876 | 2.3894 | 132599.349 | [5 empty] | 0.20515
133 |  | 109515.286 | 8.3812 | 113096.2109 |  | 28.8032 |  | 2.6184 |  | 1.6304 |  | 640.7347 | 37.0311 | 985.8379 | 130762.1816 | 0.51618 | 131282.2999 | [5 empty] | 0.47029
134 |  | 113151.8351 | 10.5413 | 112344.6831 |  | 1.4446 |  | 3.7622 |  | 1.7085 |  | 636.477 | 1.8572 | 569.5712 | 129893.2629 | 0.025888 | 129777.3113 | [5 empty] | 0.97061
135 |  | 116650.3025 | 12.268 | 111460.8089 |  | 59.0377 |  | 5.1074 |  | 1.5441 |  | 631.4695 | 75.9024 | 269.5133 | 128871.3249 | 1.058 | 128133.8796 | [5 empty] | 1.8295
136 |  | 119677.1712 | 13.4471 | 110446.7175 |  | 185.195 |  | 6.6508 |  | 1.184 |  | 625.7243 | 238.0975 | 91.8545 | 127698.8293 | 3.3189 | 126400.1288 | [5 empty] | 3.184
137 |  | 121913.1219 | 14.0708 | 109304.852 |  | 344.0191 |  | 8.3886 |  | 0.73066 |  | 619.2551 | 442.2911 | 14.8542 | 126378.601 | 6.1651 | 124619.3891 | [5 empty] | 5.1626
138 |  | 123084.7858 | 14.2242 | 108037.9633 |  | 490.318 |  | 10.3168 |  | 0.31307 |  | 612.0777 | 630.3815 | 0.13483 | 124913.8204 | 8.7869 | 122827.2719 | [5 empty] | 7.8591
139 |  | 122994.7109 | 14.0582 | 106649.1033 |  | 582.4632 |  | 12.4305 |  | 0.050056 |  | 604.2093 | 748.8488 | 7.7531 | 123308.0163 | 10.4382 | 121049.4294 | [5 empty] | 11.3052
140 |  | 121544.5715 | 13.7568 | 105141.618 |  | 594.2356 |  | 14.7248 |  | 0.016454 |  | 595.6688 | 763.984 | 10.4583 | 121565.0572 | 10.6492 | 119300.1212 | [5 empty] | 15.4524
141 |  | 118747.4134 | 13.51 | 103519.139 |  | 522.2853 |  | 17.1941 |  | 0.22182 |  | 586.4768 | 671.4806 | 2.8753 | 119689.1421 | 9.3598 | 117581.649 | [5 empty] | 20.1645
142 |  | 114726.4982 | 13.4968 | 101785.5751 |  | 387.0854 |  | 19.8325 |  | 0.60773 |  | 576.6555 | 497.6596 | 2.9083 | 117684.7903 | 6.9369 | 115884.6656 | [5 empty] | 25.2267
143 |  | 109700.7188 | 13.8815 | 99945.1025 |  | 227.1059 |  | 22.6336 |  | 1.0644 |  | 566.2285 | 291.9807 | 44.9988 | 115556.8303 | 4.0699 | 114189.3192 | [5 empty] | 30.3691
144 |  | 103959.0094 | 14.8199 | 98002.1551 |  | 87.868 |  | 25.5906 |  | 1.4618 |  | 555.2209 | 112.9682 | 167.3007 | 113310.3886 | 1.5747 | 112467.1523 | [5 empty] | 35.3023
145 |  | 97828.0942 | 16.4681 | 95961.4137 |  | 8.9906 |  | 28.6965 |  | 1.6869 |  | 543.6593 | 11.5589 | 396.6737 | 110950.8772 | 0.16112 | 110683.6332 | [5 empty] | 39.7571
146 |  | 91638.8422 | 18.9867 | 93827.7945 |  | 12.9179 |  | 31.9438 |  | 1.6757 |  | 531.5715 | 16.608 | 736.098 | 108483.9802 | 0.2315 | 108801.1598 | [5 empty] | 43.5222
147 |  | 85696.2448 | 22.5345 | 91606.4376 |  | 98.5323 |  | 35.3245 |  | 1.4314 |  | 518.9866 | 126.6789 | 1158.48 | 105915.6406 | 1.7658 | 106782.3321 | [5 empty] | 46.4723
148 |  | 80256.7176 | 27.2465 | 89302.6945 |  | 241.4729 |  | 38.8307 |  | 1.0234 |  | 505.935 | 310.4517 | 1609.0238 | 103252.0459 | 4.3274 | 104593.2548 | [5 empty] | 48.5825
149 |  | 75514.4415 | 33.202 | 86922.115 |  | 401.067 |  | 42.4538 |  | 0.56782 |  | 492.4481 | 515.6351 | 2015.8998 | 100499.6127 | 7.1875 | 102206.6088 | [5 empty] | 49.9269
150 |  | 71596.3554 | 40.3871 | 84470.4343 |  | 531.9031 |  | 46.1851 |  | 0.19437 |  | 478.5584 | 683.8458 | 2306.5372 | 97664.9721 | 9.5322 | 99604.2277 | [5 empty] | 50.6644
151 |  | 68563.7426 | 48.6632 | 81953.5587 |  | 596.753 |  | 50.0156 |  | 0.0092682 |  | 464.2993 | 767.2205 | 2425.203 | 94754.9528 | 10.6943 | 96778.9432 | [5 empty] | 51.0149
152 |  | 66417.5288 | 57.7513 | 79377.5514 |  | 577.1639 |  | 53.9361 |  | 0.065182 |  | 449.7052 | 742.0356 | 2347.0715 | 91776.5654 | 10.3433 | 93735.5183 | [5 empty] | 51.2326
153 |  | 65104.5702 | 67.2407 | 76748.6183 |  | 478.7098 |  | 57.9372 |  | 0.3462 |  | 434.8112 | 615.4573 | 2084.8849 | 88736.985 | 8.5789 | 90490.5738 | [5 empty] | 51.5812
154 |  | 64523.2151 | 76.6227 | 74073.0928 |  | 329.4051 |  | 62.0092 |  | 0.77237 |  | 419.6533 | 423.5025 | 1686.3029 | 85643.5343 | 5.9032 | 87071.5105 | [5 empty] | 52.3142
155 |  | 64527.8805 | 85.3484 | 71357.4205 |  | 171.7335 |  | 66.1423 |  | 1.2224 |  | 404.268 | 220.7906 | 1222.582 | 82503.6657 | 3.0776 | 83514.5413 | [5 empty] | 53.6622
156 |  | 64933.7774 | 92.8989 | 68608.1436 |  | 50.5591 |  | 70.3265 |  | 1.5683 |  | 388.6922 | 65.0018 | 771.5976 | 79324.9434 | 0.90606 | 79862.0337 | [5 empty] | 55.8254
157 |  | 65523.7716 | 98.8555 | 65831.8853 |  | 0.36136 |  | 74.5518 |  | 1.7116 |  | 372.9636 | 0.46459 | 399.755 | 76115.0252 | 0.0064759 | 76159.4351 | [5 empty] | 58.9675
158 |  | 66059.3625 | 102.9582 | 63035.334 |  | 35.4236 |  | 78.808 |  | 1.6115 |  | 357.1201 | 45.5427 | 147.6004 | 72881.6441 | 0.63482 | 72452.0843 | [5 empty] | 63.2093
159 |  | 66296.8652 | 105.1392 | 60225.2267 |  | 145.7692 |  | 83.0848 |  | 1.2965 |  | 341.1997 | 187.4094 | 22.866 | 69632.5896 | 2.6123 | 68782.2029 | [5 empty] | 68.6186
160 |  | 66008.3333 | 105.5276 | 57408.3333 |  | 300 |  | 87.3719 |  | 0.8563 |  | 325.2409 | 385.6975 | 2.5752 | 66375.6889 | 5.3763 | 65186.322 | [5 empty] | 75.1964
161 |  | 65005.011 | 104.4262 | 54591.4399 |  | 454.2308 |  | 91.659 |  | 0.41608 |  | 309.2821 | 583.9857 | 43.2882 | 63118.7882 | 8.1402 | 61693.3316 | [5 empty] | 82.8621
162 |  | 63159.6997 | 102.266 | 51781.3327 |  | 564.5764 |  | 95.9359 |  | 0.10111 |  | 293.3617 | 725.8524 | 96.3115 | 59869.7337 | 10.1177 | 58323.2608 | [5 empty] | 91.4413
163 |  | 60423.8236 | 99.5501 | 48984.7813 |  | 599.6386 |  | 100.192 |  | 0.0010315 |  | 277.5181 | 770.9305 | 123.3601 | 56636.3526 | 10.746 | 55086.8212 | [5 empty] | 100.6621
164 |  | 56835.4343 | 96.7979 | 46208.5231 |  | 549.4409 |  | 104.4173 |  | 0.14431 |  | 261.7895 | 706.3933 | 108.1215 | 53426.4344 | 9.8465 | 51985.6798 | [5 empty] | 110.1634
165 |  | 52515.8707 | 94.4993 | 43459.2462 |  | 428.2665 |  | 108.6016 |  | 0.49019 |  | 246.2138 | 550.6045 | 60.4314 | 50247.7121 | 7.6749 | 49013.3784 | [5 empty] | 119.5184
166 |  | 47654.9522 | 93.0839 | 40743.5738 |  | 270.5949 |  | 112.7346 |  | 0.94024 |  | 230.8284 | 347.8926 | 11.9636 | 47107.8435 | 4.8493 | 46156.7855 | [5 empty] | 128.2716
167 |  | 42486.9107 | 92.906 | 38068.0483 |  | 121.2902 |  | 116.8066 |  | 1.3664 |  | 215.6705 | 155.9378 | 4.8322 | 44014.3928 | 2.1736 | 43397.9526 | [5 empty] | 135.9853
168 |  | 37261.1653 | 94.2401 | 35439.1153 |  | 22.8361 |  | 120.8077 |  | 1.6474 |  | 200.7766 | 29.3595 | 76.5822 | 40974.8124 | 0.40924 | 40716.2339 | [5 empty] | 142.2889
169 |  | 32213.0311 | 97.2799 | 32863.108 |  | 3.247 |  | 124.7282 |  | 1.7033 |  | 186.1825 | 4.1746 | 246.115 | 37996.425 | 0.05819 | 38090.5259 | [5 empty] | 146.9231
170 |  | 27539.2756 | 102.1354 | 30346.2323 |  | 68.0969 |  | 128.5587 |  | 1.5182 |  | 171.9234 | 87.5493 | 504.844 | 35086.4058 | 1.2204 | 35501.4756 | [5 empty] | 149.7713
171 |  | 23382.1587 | 108.8223 | 27894.5516 |  | 198.933 |  | 132.29 |  | 1.1448 |  | 158.0336 | 255.76 | 815.8815 | 32251.7651 | 3.5651 | 32933.5017 | [5 empty] | 150.8726
172 |  | 19823.5489 | 117.2449 | 25513.9722 |  | 358.5271 |  | 135.9131 |  | 0.68925 |  | 144.5467 | 460.9434 | 1121.7376 | 29499.332 | 6.4251 | 30376.473 | [5 empty] | 150.4156
173 |  | 16888.4483 | 127.1768 | 23210.2291 |  | 501.4677 |  | 139.4193 |  | 0.28125 |  | 131.4951 | 644.7162 | 1358.5412 | 26835.7372 | 8.9867 | 27826.8961 | [5 empty] | 148.7142
174 |  | 14555.3586 | 138.2477 | 20988.8722 |  | 587.0821 |  | 142.8001 |  | 0.036872 |  | 118.9102 | 754.7871 | 1472.8698 | 24267.3976 | 10.521 | 25288.498 | [5 empty] | 146.1708
175 |  | 12769.8468 | 149.9449 | 18855.253 |  | 591.0094 |  | 146.0473 |  | 0.025662 |  | 106.8225 | 759.8362 | 1436.4571 | 21800.5006 | 10.5914 | 22772.1284 | [5 empty] | 143.2337
176 |  | 11457.6573 | 161.6365 | 16814.5115 |  | 512.132 |  | 149.1532 |  | 0.25081 |  | 95.2608 | 658.4269 | 1254.5762 | 19440.9892 | 9.1778 | 20294.978 | [5 empty] | 140.3547
177 |  | 10534.6736 | 172.6184 | 14871.5641 |  | 372.8941 |  | 152.1102 |  | 0.64824 |  | 84.2533 | 479.4144 | 965.6241 | 17194.5475 | 6.6826 | 17879.1798 | [5 empty] | 137.9541
178 |  | 9912.6343 | 182.1816 | 13031.0916 |  | 212.9146 |  | 154.9113 |  | 1.1049 |  | 73.8263 | 273.7355 | 631.8775 | 15066.5875 | 3.8156 | 15549.9373 | [5 empty] | 136.3943
179 |  | 9501.2268 | 189.6916 | 11297.5276 |  | 77.7147 |  | 157.5497 |  | 1.4908 |  | 64.005 | 99.9145 | 323.8573 | 13062.2357 | 1.3927 | 13333.3835 | [5 empty] | 135.963
180 |  | 9208.4954 | 194.6646 | 9675.0487 |  | 5.7644 |  | 160.019 |  | 1.6962 |  | 54.813 | 7.4111 | 102.534 | 11186.3206 | 0.1033 | 11254.4116 | [5 empty] | 136.8635
181 |  | 8942.0223 | 196.8303 | 8167.5634 |  | 17.5368 |  | 162.3133 |  | 1.6626 |  | 46.2725 | 22.5463 | 4.2193 | 9443.3615 | 0.31427 | 9334.7207 | [5 empty] | 139.2092
182 |  | 8612.9165 | 196.1661 | 6778.7034 |  | 109.682 |  | 164.4271 |  | 1.3995 |  | 38.404 | 141.0136 | 32.2376 | 7837.5574 | 1.9656 | 7591.2855 | [5 empty] | 143.0192
183 |  | 8143.4378 | 192.899 | 5511.8147 |  | 255.9809 |  | 166.3552 |  | 0.98195 |  | 31.2266 | 329.104 | 157.5815 | 6372.7768 | 4.5874 | 6035.4025 | [5 empty] | 148.2133
184 |  | 7477.468 | 187.4743 | 4369.9492 |  | 414.805 |  | 168.093 |  | 0.52861 |  | 24.7575 | 533.2976 | 328.2455 | 5052.5485 | 7.4337 | 4672.3796 | [5 empty] | 154.6086
185 |  | 6591.55 | 180.4981 | 3355.8578 |  | 540.9623 |  | 169.6364 |  | 0.16851 |  | 19.0123 | 695.4927 | 484.5233 | 3880.0529 | 9.6945 | 3501.8547 | [5 empty] | 161.918
186 |  | 5503.3309 | 172.665 | 2471.9836 |  | 598.5554 |  | 170.9816 |  | 0.0041233 |  | 14.0048 | 769.5378 | 575.9161 | 2858.1149 | 10.7266 | 2518.6534 | [5 empty] | 169.7576
187 |  | 4274.2961 | 164.684 | 1720.4558 |  | 571.1968 |  | 172.1254 |  | 0.082214 |  | 9.7471 | 734.364 | 574.9024 | 1989.1962 | 10.2363 | 1714.041 | [5 empty] | 177.663
188 |  | 3004.7165 | 157.2144 | 1103.085 |  | 466.6711 |  | 173.065 |  | 0.38057 |  | 6.2494 | 599.9796 | 483.7624 | 1275.3903 | 8.3631 | 1077.1981 | [5 empty] | 185.12
189 |  | 1820.5089 | 150.8199 | 621.3585 |  | 314.7203 |  | 173.7982 |  | 0.81429 |  | 3.5202 | 404.6228 | 332.6614 | 718.4166 | 5.6401 | 596.7474 | [5 empty] | 191.6058
190 |  | 853.7665 | 145.9425 | 276.4368 |  | 158.581 |  | 174.3231 |  | 1.26 |  | 1.5661 | 203.881 | 169.709 | 319.6171 | 2.8419 | 262.1822 | [5 empty] | 196.6386
191 |  | 220.4869 | 142.894 | 69.1509 |  | 42.6814 |  | 174.6386 |  | 1.5908 |  | 0.39177 | 54.8737 | 45.9924 | 79.9524 | 0.76489 | 65.077 | [5 empty] | 199.8284
192 |  | 2.5059e-26 | 141.8577 | 3.8776e-27 |  | 9.2216e-27 |  | 174.7438 |  | 1.7126 |  | 2.1968e-29 | 1.1856e-26 | 1.0857e-26 | 4.4833e-27 | 1.6526e-28 | 2.9271e-27 | [5 empty] | 200.9211
193 |  | 220.4869 | 142.894 | 69.1509 |  | 42.6814 |  | 174.6386 |  | 1.5908 |  | 0.39177 | 54.8737 | 45.9924 | 79.9524 | 0.76489 | 65.077 | [5 empty] | 199.8284
194 |  | 853.7665 | 145.9425 | 276.4368 |  | 158.581 |  | 174.3231 |  | 1.26 |  | 1.5661 | 203.881 | 169.709 | 319.6171 | 2.8419 | 262.1822 | [5 empty] | 196.6386
195 |  | 1820.5089 | 150.8199 | 621.3585 |  | 314.7203 |  | 173.7982 |  | 0.81429 |  | 3.5202 | 404.6228 | 332.6614 | 718.4166 | 5.6401 | 596.7474 | [5 empty] | 191.6058
196 |  | 3004.7165 | 157.2144 | 1103.085 |  | 466.6711 |  | 173.065 |  | 0.38057 |  | 6.2494 | 599.9796 | 483.7624 | 1275.3903 | 8.3631 | 1077.1981 | [5 empty] | 185.12
197 |  | 4274.2961 | 164.684 | 1720.4558 |  | 571.1968 |  | 172.1254 |  | 0.082214 |  | 9.7471 | 734.364 | 574.9024 | 1989.1962 | 10.2363 | 1714.041 | [5 empty] | 177.663
198 |  | 5503.3309 | 172.665 | 2471.9836 |  | 598.5554 |  | 170.9816 |  | 0.0041233 |  | 14.0048 | 769.5378 | 575.9161 | 2858.1149 | 10.7266 | 2518.6534 | [5 empty] | 169.7576
199 |  | 6591.55 | 180.4981 | 3355.8578 |  | 540.9623 |  | 169.6364 |  | 0.16851 |  | 19.0123 | 695.4927 | 484.5233 | 3880.0529 | 9.6945 | 3501.8547 | [5 empty] | 161.918
200 |  | 7477.468 | 187.4743 | 4369.9492 |  | 414.805 |  | 168.093 |  | 0.52861 |  | 24.7575 | 533.2976 | 328.2455 | 5052.5485 | 7.4337 | 4672.3796 | [5 empty] | 154.6086
201 |  | 8143.4378 | 192.899 | 5511.8147 |  | 255.9809 |  | 166.3552 |  | 0.98195 |  | 31.2266 | 329.104 | 157.5815 | 6372.7768 | 4.5874 | 6035.4025 | [5 empty] | 148.2133
202 |  | 8612.9165 | 196.1661 | 6778.7034 |  | 109.682 |  | 164.4271 |  | 1.3995 |  | 38.404 | 141.0136 | 32.2376 | 7837.5574 | 1.9656 | 7591.2855 | [5 empty] | 143.0192
203 |  | 8942.0223 | 196.8303 | 8167.5634 |  | 17.5368 |  | 162.3133 |  | 1.6626 |  | 46.2725 | 22.5463 | 4.2193 | 9443.3615 | 0.31427 | 9334.7207 | [5 empty] | 139.2092
204 |  | 9208.4954 | 194.6646 | 9675.0487 |  | 5.7644 |  | 160.019 |  | 1.6962 |  | 54.813 | 7.4111 | 102.534 | 11186.3206 | 0.1033 | 11254.4116 | [5 empty] | 136.8635
205 |  | 9501.2268 | 189.6916 | 11297.5276 |  | 77.7147 |  | 157.5497 |  | 1.4908 |  | 64.005 | 99.9145 | 323.8573 | 13062.2357 | 1.3927 | 13333.3835 | [5 empty] | 135.963
206 |  | 9912.6343 | 182.1816 | 13031.0916 |  | 212.9146 |  | 154.9113 |  | 1.1049 |  | 73.8263 | 273.7355 | 631.8775 | 15066.5875 | 3.8156 | 15549.9373 | [5 empty] | 136.3943
207 |  | 10534.6736 | 172.6184 | 14871.5641 |  | 372.8941 |  | 152.1102 |  | 0.64824 |  | 84.2533 | 479.4144 | 965.6241 | 17194.5475 | 6.6826 | 17879.1798 | [5 empty] | 137.9541
208 |  | 11457.6573 | 161.6365 | 16814.5115 |  | 512.132 |  | 149.1532 |  | 0.25081 |  | 95.2608 | 658.4269 | 1254.5762 | 19440.9892 | 9.1778 | 20294.978 | [5 empty] | 140.3547
209 |  | 12769.8468 | 149.9449 | 18855.253 |  | 591.0094 |  | 146.0473 |  | 0.025662 |  | 106.8225 | 759.8362 | 1436.4571 | 21800.5006 | 10.5914 | 22772.1284 | [5 empty] | 143.2337
210 |  | 14555.3586 | 138.2477 | 20988.8722 |  | 587.0821 |  | 142.8001 |  | 0.036872 |  | 118.9102 | 754.7871 | 1472.8698 | 24267.3976 | 10.521 | 25288.498 | [5 empty] | 146.1708
211 |  | 16888.4483 | 127.1768 | 23210.2291 |  | 501.4677 |  | 139.4193 |  | 0.28125 |  | 131.4951 | 644.7162 | 1358.5412 | 26835.7372 | 8.9867 | 27826.8961 | [5 empty] | 148.7142
212 |  | 19823.5489 | 117.2449 | 25513.9722 |  | 358.5271 |  | 135.9131 |  | 0.68925 |  | 144.5467 | 460.9434 | 1121.7376 | 29499.332 | 6.4251 | 30376.473 | [5 empty] | 150.4156
213 |  | 23382.1587 | 108.8223 | 27894.5516 |  | 198.933 |  | 132.29 |  | 1.1448 |  | 158.0336 | 255.76 | 815.8815 | 32251.7651 | 3.5651 | 32933.5017 | [5 empty] | 150.8726
214 |  | 27539.2756 | 102.1354 | 30346.2323 |  | 68.0969 |  | 128.5587 |  | 1.5182 |  | 171.9234 | 87.5493 | 504.844 | 35086.4058 | 1.2204 | 35501.4756 | [5 empty] | 149.7713
215 |  | 32213.0311 | 97.2799 | 32863.108 |  | 3.247 |  | 124.7282 |  | 1.7033 |  | 186.1825 | 4.1746 | 246.115 | 37996.425 | 0.05819 | 38090.5259 | [5 empty] | 146.9231
216 |  | 37261.1653 | 94.2401 | 35439.1153 |  | 22.8361 |  | 120.8077 |  | 1.6474 |  | 200.7766 | 29.3595 | 76.5822 | 40974.8124 | 0.40924 | 40716.2339 | [5 empty] | 142.2889
217 |  | 42486.9107 | 92.906 | 38068.0483 |  | 121.2902 |  | 116.8066 |  | 1.3664 |  | 215.6705 | 155.9378 | 4.8322 | 44014.3928 | 2.1736 | 43397.9526 | [5 empty] | 135.9853
218 |  | 47654.9522 | 93.0839 | 40743.5738 |  | 270.5949 |  | 112.7346 |  | 0.94024 |  | 230.8284 | 347.8926 | 11.9636 | 47107.8435 | 4.8493 | 46156.7855 | [5 empty] | 128.2716
219 |  | 52515.8707 | 94.4993 | 43459.2462 |  | 428.2665 |  | 108.6016 |  | 0.49019 |  | 246.2138 | 550.6045 | 60.4314 | 50247.7121 | 7.6749 | 49013.3784 | [5 empty] | 119.5184
220 |  | 56835.4343 | 96.7979 | 46208.5231 |  | 549.4409 |  | 104.4173 |  | 0.14431 |  | 261.7895 | 706.3933 | 108.1215 | 53426.4344 | 9.8465 | 51985.6798 | [5 empty] | 110.1634
221 |  | 60423.8236 | 99.5501 | 48984.7813 |  | 599.6386 |  | 100.192 |  | 0.0010315 |  | 277.5181 | 770.9305 | 123.3601 | 56636.3526 | 10.746 | 55086.8212 | [5 empty] | 100.6621
222 |  | 63159.6997 | 102.266 | 51781.3327 |  | 564.5764 |  | 95.9359 |  | 0.10111 |  | 293.3617 | 725.8524 | 96.3115 | 59869.7337 | 10.1177 | 58323.2608 | [5 empty] | 91.4413
223 |  | 65005.011 | 104.4262 | 54591.4399 |  | 454.2308 |  | 91.659 |  | 0.41608 |  | 309.2821 | 583.9857 | 43.2882 | 63118.7882 | 8.1402 | 61693.3316 | [5 empty] | 82.8621
224 |  | 66008.3333 | 105.5276 | 57408.3333 |  | 300 |  | 87.3719 |  | 0.8563 |  | 325.2409 | 385.6975 | 2.5752 | 66375.6889 | 5.3763 | 65186.322 | [5 empty] | 75.1964
225 |  | 66296.8652 | 105.1392 | 60225.2267 |  | 145.7692 |  | 83.0848 |  | 1.2965 |  | 341.1997 | 187.4094 | 22.866 | 69632.5896 | 2.6123 | 68782.2029 | [5 empty] | 68.6186
226 |  | 66059.3625 | 102.9582 | 63035.334 |  | 35.4236 |  | 78.808 |  | 1.6115 |  | 357.1201 | 45.5427 | 147.6004 | 72881.6441 | 0.63482 | 72452.0843 | [5 empty] | 63.2093
227 |  | 65523.7716 | 98.8555 | 65831.8853 |  | 0.36136 |  | 74.5518 |  | 1.7116 |  | 372.9636 | 0.46459 | 399.755 | 76115.0252 | 0.0064759 | 76159.4351 | [5 empty] | 58.9675
228 |  | 64933.7774 | 92.8989 | 68608.1436 |  | 50.5591 |  | 70.3265 |  | 1.5683 |  | 388.6922 | 65.0018 | 771.5976 | 79324.9434 | 0.90606 | 79862.0337 | [5 empty] | 55.8254
229 |  | 64527.8805 | 85.3484 | 71357.4205 |  | 171.7335 |  | 66.1423 |  | 1.2224 |  | 404.268 | 220.7906 | 1222.582 | 82503.6657 | 3.0776 | 83514.5413 | [5 empty] | 53.6622
230 |  | 64523.2151 | 76.6227 | 74073.0928 |  | 329.4051 |  | 62.0092 |  | 0.77237 |  | 419.6533 | 423.5025 | 1686.3029 | 85643.5343 | 5.9032 | 87071.5105 | [5 empty] | 52.3142
231 |  | 65104.5702 | 67.2407 | 76748.6183 |  | 478.7098 |  | 57.9372 |  | 0.3462 |  | 434.8112 | 615.4573 | 2084.8849 | 88736.985 | 8.5789 | 90490.5738 | [5 empty] | 51.5812
232 |  | 66417.5288 | 57.7513 | 79377.5514 |  | 577.1639 |  | 53.9361 |  | 0.065182 |  | 449.7052 | 742.0356 | 2347.0715 | 91776.5654 | 10.3433 | 93735.5183 | [5 empty] | 51.2326
233 |  | 68563.7426 | 48.6632 | 81953.5587 |  | 596.753 |  | 50.0156 |  | 0.0092682 |  | 464.2993 | 767.2205 | 2425.203 | 94754.9528 | 10.6943 | 96778.9432 | [5 empty] | 51.0149
234 |  | 71596.3554 | 40.3871 | 84470.4343 |  | 531.9031 |  | 46.1851 |  | 0.19437 |  | 478.5584 | 683.8458 | 2306.5372 | 97664.9721 | 9.5322 | 99604.2277 | [5 empty] | 50.6644
235 |  | 75514.4415 | 33.202 | 86922.115 |  | 401.067 |  | 42.4538 |  | 0.56782 |  | 492.4481 | 515.6351 | 2015.8998 | 100499.6127 | 7.1875 | 102206.6088 | [5 empty] | 49.9269
236 |  | 80256.7176 | 27.2465 | 89302.6945 |  | 241.4729 |  | 38.8307 |  | 1.0234 |  | 505.935 | 310.4517 | 1609.0238 | 103252.0459 | 4.3274 | 104593.2548 | [5 empty] | 48.5825
237 |  | 85696.2448 | 22.5345 | 91606.4376 |  | 98.5323 |  | 35.3245 |  | 1.4314 |  | 518.9866 | 126.6789 | 1158.48 | 105915.6406 | 1.7658 | 106782.3321 | [5 empty] | 46.4723
238 |  | 91638.8422 | 18.9867 | 93827.7945 |  | 12.9179 |  | 31.9438 |  | 1.6757 |  | 531.5715 | 16.608 | 736.098 | 108483.9802 | 0.2315 | 108801.1598 | [5 empty] | 43.5222
239 |  | 97828.0942 | 16.4681 | 95961.4137 |  | 8.9906 |  | 28.6965 |  | 1.6869 |  | 543.6593 | 11.5589 | 396.6737 | 110950.8772 | 0.16112 | 110683.6332 | [5 empty] | 39.7571
240 |  | 103959.0094 | 14.8199 | 98002.1551 |  | 87.868 |  | 25.5906 |  | 1.4618 |  | 555.2209 | 112.9682 | 167.3007 | 113310.3886 | 1.5747 | 112467.1523 | [5 empty] | 35.3023
241 |  | 109700.7188 | 13.8815 | 99945.1025 |  | 227.1059 |  | 22.6336 |  | 1.0644 |  | 566.2285 | 291.9807 | 44.9988 | 115556.8303 | 4.0699 | 114189.3192 | [5 empty] | 30.3691
242 |  | 114726.4982 | 13.4968 | 101785.5751 |  | 387.0854 |  | 19.8325 |  | 0.60773 |  | 576.6555 | 497.6596 | 2.9083 | 117684.7903 | 6.9369 | 115884.6656 | [5 empty] | 25.2267
243 |  | 118747.4134 | 13.51 | 103519.139 |  | 522.2853 |  | 17.1941 |  | 0.22182 |  | 586.4768 | 671.4806 | 2.8753 | 119689.1421 | 9.3598 | 117581.649 | [5 empty] | 20.1645
244 |  | 121544.5715 | 13.7568 | 105141.618 |  | 594.2356 |  | 14.7248 |  | 0.016454 |  | 595.6688 | 763.984 | 10.4583 | 121565.0572 | 10.6492 | 119300.1212 | [5 empty] | 15.4524
245 |  | 122994.7109 | 14.0582 | 106649.1033 |  | 582.4632 |  | 12.4305 |  | 0.050056 |  | 604.2093 | 748.8488 | 7.7531 | 123308.0163 | 10.4382 | 121049.4294 | [5 empty] | 11.3052
246 |  | 123084.7858 | 14.2242 | 108037.9633 |  | 490.318 |  | 10.3168 |  | 0.31307 |  | 612.0777 | 630.3815 | 0.13483 | 124913.8204 | 8.7869 | 122827.2719 | [5 empty] | 7.8591
247 |  | 121913.1219 | 14.0708 | 109304.852 |  | 344.0191 |  | 8.3886 |  | 0.73066 |  | 619.2551 | 442.2911 | 14.8542 | 126378.601 | 6.1651 | 124619.3891 | [5 empty] | 5.1626
248 |  | 119677.1712 | 13.4471 | 110446.7175 |  | 185.195 |  | 6.6508 |  | 1.184 |  | 625.7243 | 238.0975 | 91.8545 | 127698.8293 | 3.3189 | 126400.1288 | [5 empty] | 3.184
249 |  | 116650.3025 | 12.268 | 111460.8089 |  | 59.0377 |  | 5.1074 |  | 1.5441 |  | 631.4695 | 75.9024 | 269.5133 | 128871.3249 | 1.058 | 128133.8796 | [5 empty] | 1.8295
250 |  | 113151.8351 | 10.5413 | 112344.6831 |  | 1.4446 |  | 3.7622 |  | 1.7085 |  | 636.477 | 1.8572 | 569.5712 | 129893.2629 | 0.025888 | 129777.3113 | [5 empty] | 0.97061
251 |  | 109515.286 | 8.3812 | 113096.2109 |  | 28.8032 |  | 2.6184 |  | 1.6304 |  | 640.7347 | 37.0311 | 985.8379 | 130762.1816 | 0.51618 | 131282.2999 | [5 empty] | 0.47029
252 |  | 106059.4051 | 6.0017 | 113713.5816 |  | 133.3289 |  | 1.6788 |  | 1.332 |  | 644.2323 | 171.4155 | 1480.2722 | 131475.9876 | 2.3894 | 132599.349 | [5 empty] | 0.20515
253 |  | 103065.2292 | 3.6874 | 114195.3081 |  | 285.2797 |  | 0.94567 |  | 0.89832 |  | 646.9615 | 366.7723 | 1987.9771 | 132032.9612 | 5.1125 | 133681.2569 | [5 empty] | 0.078606
254 |  | 100760.5046 | 1.7461 | 114540.2299 |  | 441.419 |  | 0.42072 |  | 0.45265 |  | 648.9156 | 567.5141 | 2430.1328 | 132431.7607 | 7.9106 | 134486.7333 | [5 empty] | 0.024761
255 |  | 99310.9702 | 0.45354 | 114747.5158 |  | 557.3186 |  | 0.10524 |  | 0.12183 |  | 650.09 | 716.5214 | 2731.6071 | 132671.4254 | 9.9876 | 134983.6491 | [5 empty] | 0.0048362
|  |  | 9.393 |  |  |  |  | 9.3473 | [14 empty] | 9.3717